## FM_Dashboard
AKA | AGA KHAN ACADEMY ¦ FACILITY MANAGEMENT MIS DASHBOARD
HYDERABAD · FM | Calendar 2026 • live MIS data Jan-26 to Aug-26 • Water · Energy · Solar · HVAC · Treatment · Service desk · Manpower • 1,354 occupants • 52,652 m² built-up
| MONTH |  |  |  |  | FACILITY | [7 empty] | Showing: Aug-26 • Facility drill: All Facilities • Data completeness 88%
▶ FM Dashboard | 📅 Select ▸ | Aug-26 |  |  |  | 🏢 Drill ▸ |  | All Facilities | [5 empty] | Pick a month (or 2026 YTD) from the yellow drop-down; the facility drop-down drives the drill-down charts & highlights the scorecard. 'vs 2025' compares the monthly average with the Avg-2025 row of each source sheet.
Per-Capita Pyramid | 💧 WATER CONSUMED (kL) |  |  | 🚰 LPCD (L / person / day) |  |  |  | ⛲ BOREWELL DRAW (kL) |  |  |  | ⚡ HT GRID ENERGY (kWh) |  |  |  | ₹ ENERGY BILL (₹ Lakh) |  |  | 🏢 EPI (kWh / m² / month)
| 14026 |  |  | 334.1592 |  |  |  | 11995 |  |  |  | 146382 |  |  |  | 18.2957 |  |  | 2.7802
Monthly KPI | Avg/month 14,026 • vs Avg-2025 -86% |  |  | Benchmark 135 • ▲ 2.5× benchmark |  |  |  | STP recycled 2,683 kL (18% of inlet) |  |  |  | Avg/month 1,46,382 • vs Avg-2025 +10% |  |  |  | ₹11.70/kVAh • bill vs Avg-2025 +5% |  |  | Benchmark ≤ 8 • ✔ on target
Complaints | 🔌 POWER FACTOR |  |  | ☀ SOLAR GENERATION (kWh) |  |  |  | ❄ HVAC ENERGY (kWh) |  |  |  | 🎫 COMPLAINTS RECEIVED |  |  |  | 👷 TECH DEPLOYMENT |  |  | 🚿 WTP TREATED WATER (kL)
| 0.93619 |  |  | 115911 |  |  |  | 21957.88 |  |  |  | 216 |  |  |  | 84.84% |  |  | 10986
Water - Bldg | Target 0.95 • ▲ below target • MD 37% of sanctioned |  |  | Savings ₹13.7 L • vs Avg-2025 +35% |  |  |  | vs Avg-2025 +5% |  |  |  | Closure 68% • Pending – • 5 months logged |  |  |  | Target 90% • Present 543 / 640 man-days |  |  | Avg/month 10,986 • vs Avg-2025 +2% • Drip 2,501 kL
LPCD
Water Quality
Power
EPI
Power - Bldg
Solar
HVAC
DG / Outages
Tech Manpower
Attendance
Building Master
Calc engine
🏢 FACILITY SCORECARD (month filter applies • selected facility highlighted • LPCD and kWh/person are per resident student, residences only; SR-1+SR-2 and SR-3+SR-4 are each one block)
| Facility |  | Group |  | Water kL / mo |  | Water vs baseline |  | Water share |  | Power kWh / mo |  | Power vs Avg-2025 |  | Power share |  | Water YTD kL | Power YTD kWh |  | LPCD | kWh / person
| SR-1 |  | Residence |  | 329 |  | -15.32% |  | 4.681% |  | 4790 |  | 81.99% |  | 3.31% |  | 1817 | 32957 |  | 713.0145 | 326.9655
| SR-2 |  | Residence |  | 312 |  | 56.52% |  | 4.439% |  | 4692 |  | 55.03% |  | 3.243% |  | 1531 | 33862 |  | with SR-1 | with SR-1
| SR-3 |  | Residence |  | 64 |  | -62.65% |  | 0.9106% |  | 5092 |  | 58.29% |  | 3.519% |  | 628 | 30031 |  | 252.1994 | 348.4848
| SR-4 |  | Residence |  | 194 |  | 19.69% |  | 2.76% |  | 6408 |  | 77.77% |  | 4.428% |  | 1740 | 51868 |  | with SR-3 | with SR-3
| SR-9/10 A |  | Residence |  | 1468 |  | 220% |  | 20.89% |  | 3576 |  | -36.87% |  | 2.471% |  | 7012 | 43986 |  | 1076.2463 | 81.2727
| SR-9/10 B |  | Residence |  | 45 |  | -90.09% |  | 0.6403% |  | 12306 |  | 125% |  | 8.504% |  | 999 | 67455 |  | 85.389 | 723.8824
| SR-11/12 CA |  | Residence |  | 710 |  | 108.1% |  | 10.1% |  | 5498 |  | 19.54% |  | 3.8% |  | 3147 | 50546 |  | 558.6153 | 134.0976
| SR-11/12 CB |  | Residence |  | 0 |  | -100% |  | 0% |  | 8718 |  | 67.56% |  | 6.025% |  | 1205 | 68631 |  | 0 | 311.3571
| Junior School |  | Academic |  | 120 |  | -76.61% |  | 1.707% |  | 10905 |  | 29.23% |  | 7.536% |  | 358 | 79142 |  | – | –
| Senior School 1 & 3 |  | Academic |  | 82 |  | -82.42% |  | 1.167% |  | 8760 |  | -8.951% |  | 6.054% |  | 482 | 86779 |  | – | –
| Senior School 2 |  | Academic |  | 45 |  | 33% |  | 0.6403% |  | 8229 |  | 9.505% |  | 5.687% |  | 558 | 69436 |  | – | –
| Academy Building |  | Academic |  | 38 |  | 334.3% |  | 0.5407% |  | 18300 |  | -0.5885% |  | 12.65% |  | 809 | 154300 |  | – | –
| Commons |  | Amenity |  | 1094 |  | 497% |  | 15.57% |  | 25640 |  | 1.037% |  | 17.72% |  | 3314 | 168440 |  | – | –
| Athletic Centre |  | Amenity |  | 54 |  | -88.44% |  | 0.7684% |  | 9768 |  | 71.69% |  | 6.751% |  | 801 | 63308 |  | – | –
| Swimming Pool |  | Amenity |  | 1559 |  | 244.2% |  | 22.18% |  | – |  | – |  | – |  | 6554 | – |  | – | –
| PCM |  | Support |  | 570 |  | -50.03% |  | 8.11% |  | 3784 |  | 14.58% |  | 2.615% |  | 4155 | 28363 |  | – | –
| Nursery |  | Support |  | 209 |  | – |  | 2.974% |  | 4852 |  | 92.91% |  | 3.353% |  | 887 | 31620.7 |  | – | –
| Laundry |  | Support |  | 135 |  | – |  | 1.921% |  | 3382 |  | 24.96% |  | 2.337% |  | 690 | 23054 |  | – | –
| METERED FACILITIES |  |  |  | 7028 |  |  |  | 100% |  | 144700 |  |  |  | 100% |  | 36687 | 1083778.7
| 🚨 WATCHLIST (live, follows month filter) | [10 empty] | 🔎 DATA-QUALITY FINDINGS IN SOURCE SHEETS (please verify)
| LPCD vs benchmark (L/person/day) | [6 empty] | 334.1592 |  | ▲ Act |  | 1. DG Units Generated, Mar–Aug 2026: total units are typed (11–56 kWh) and do not equal 500 kVA + 750 kVA (44–150 kWh), while diesel reads 8,735–17,820 L against 266–1,523 L in Jan–Feb — verify against the DG log.
| Power factor vs 0.95 target | [6 empty] | 0.93619 |  | ▲ Act |  | 2. Complaints summary: no entries for Mar–May 2026, and the pending column is blank from Jun-26 — please verify.
| EPI vs 8 kWh/m² benchmark | [6 empty] | 2.7802 |  | ✔ OK |  | 3. WQ sheet: Bore 08 and Bore 10 values look shifted by one row (e.g. Turbidity 912/840 NTU, pH 360/150).
| Technical deployment vs 90% target | [6 empty] | 84.84% |  | ▲ Act |  | 4. Building wise water: 13 meters flag 'VERIFY AVG-2025 (>3× prior yrs)'; building comparisons therefore use the median 2023–25 baseline.
| Months of complaint data missing (to latest month) | [6 empty] | 3 |  | ▲ Act |  | 5. Technical manpower cost invoices are logged only for Jan–Feb 2026.
| Months of tech-manpower invoices missing | [6 empty] | 6 |  | ▲ Act |  | 6. LPCD sheet Avg-2025 (2,432 L/person/day; 100,169 kL/month) is more than 2× Avg-2023/2024, so water comparisons against 2025 overstate the 2026 improvement.
| Data completeness vs 80% | [6 empty] | 87.5% |  | ✔ OK |  | 7. LPCD sheet water (e.g. Jan-26 40,704 kL) is about twice the metered inlet on Building wise water (borewells + STP outlet 18,598 kL) — confirm which basis LPCD should use.
| Water-meter data-quality flags open | [6 empty] | 14 |  | ▲ Act |  | 8. Solar Power: Apr-26 export (227,564 kWh) exceeds generation (136,018 kWh) and Jun–Aug export equals generation exactly; savings are computed from export — verify the export readings.
| Borewell/WQ parameters above limit | [6 empty] | 8 |  | ▲ Act |  | 9. Building_Master: resident-student headcount (192, 2026-27 roster) is entered for the SR residences only. Other facilities' occupants and all floor areas are blank, and staff living in the residences are not counted, so residence LPCD is per student.
| HVAC energy vs Avg-2025 | [6 empty] | 4.866% |  | ✔ OK
| HT energy bill vs Avg-2025 | [6 empty] | 5.069% |  | ✔ OK
| Power failures per month (vs Avg-2025) | [6 empty] | 1 |  | ✔ OK
Sources: Complaints summary, LPCD, Building wise water, Power data, EPI, Power Building wise, Solar Power, HVAC consumption, Technical manpower cost, Attendance, DG Units Generated, WQ, Monthly KPI Report — all linked live via MIS_Calc. Benchmarks: LPCD 135 (LPCD sheet), EPI 8 (EPI sheet), PF 0.95 & deployment 90% (MIS_Calc B10:B11).

## PerCapita_Pyramid
AKA | ▲ AGA KHAN ACADEMY ¦ PER-CAPITA PERFORMANCE PYRAMID
OFFICIAL MIS | Live MIS data Jan-26 to Aug-26 • 1,354 occupants (LPCD sheet) • 52,652 m² • 100 = Avg-2025 baseline, above 100 = better
| MONTH |  |  |  |  | Showing: Aug-26 ¦ population base 1,354 persons • 31.0 days
FM Dashboard | 📅 Select ▸ | Aug-26 |  |  |  | Per-person figures divide by campus occupants from the LPCD sheet; building pyramids use absolute kL / kWh per month (residence LPCD on FM_Dashboard uses the resident-student headcount in Building_Master). KPIs with no data for the month or no 2025 baseline are shown but not scored.
▶ Per-Capita Pyramid | ▲ PERFORMANCE PYRAMID — apex index → pillars → categories → key per-capita KPIs → operational detail (score 100 = Avg-2025 • above 100 = better)
Monthly KPI | TIER 1 · APEX One composite score for the campus vs its own 2025 performance | [7 empty] | ▲ PER-CAPITA PERFORMANCE INDEX | [6 empty] | Scored on 18 core per-capita KPIs across 6 domains 8 better • 4 in line • 7 watch • 7 no data
105.2045
Complaints | [8 empty] | ✔ Better than 2025
INDEX SCORE • 100 = Avg-2025 • +5.2 pts vs 2025
Water - Bldg
| TIER 2 · PILLARS Utilities · Sustainability · Operations |  |  |  |  | ⚡💧 UTILITIES |  |  |  | ☀♻ SUSTAINABILITY |  |  |  | 🛠 OPERATIONS |  |  |  |  | Pillar = average of its two category scores Colour key (pillar → category → KPI tile → chart): Blue = Utilities • Green = Sustainability Purple = Operations
LPCD | [5 empty] | 121.9023 |  |  |  | 113.2711 |  |  |  | 80.4401
[6 empty] | ✔ Better than 2025 |  |  |  | ✔ Better than 2025 |  |  |  | ▲ Below 2025
Water Quality | [5 empty] | PILLAR SCORE = avg(Energy, Water) |  |  |  | PILLAR SCORE = avg(Solar, Treatment) |  |  |  | PILLAR = avg(Service Desk, People & Cost)
Power | TIER 3 · CATEGORIES 6 MIS domains |  | ⚡ ENERGY |  |  | 💧 WATER |  |  | ☀ SOLAR |  |  | ♻ TREATMENT & REUSE |  |  | 🎫 SERVICE DESK |  |  | 👷 PEOPLE & COST |  |  | Score = avg of core KPI scores (each capped 50–150)
|  |  | 93.8046 |  |  | 150 |  |  | 128.7593 |  |  | 97.7828 |  |  | 58.7963 |  |  | 102.0839
EPI |  |  | 108.1 kWh/p/mo |  |  | 334.2 LPCD |  |  | 85.6 kWh/p/mo |  |  | 63.9 L/p/day STP |  |  | 15.95 /100p/mo |  |  | OPEX not yet invoiced
|  |  | SCORE • 5 of 5 KPIs |  |  | SCORE • 2 of 2 KPIs |  |  | SCORE • 2 of 2 KPIs |  |  | SCORE • 2 of 2 KPIs |  |  | SCORE • 2 of 3 KPIs |  |  | SCORE • 1 of 4 KPIs
Power - Bldg
TIER 4 · 12 KEY KPIs grouped by pillar — Utilities (6) · Sustainability (2) · Operations (4) (selected month / YTD average • Δ vs Avg-2025)
Solar | ⚡ Grid kWh | ₹ Energy |  | ❄ HVAC |  | 🏢 EPI |  | 💧 LPCD |  | ⛲ Borewell |  | ☀ Solar |  | ♻ STP |  | 🎫 Complaints |  | ✅ Closure |  | 💰 OPEX |  | 👷 Staff
| 108.1108 | 1351.2341 |  | 16.217 |  | 2.7802 |  | 334.1592 |  | 285.7721 |  | 85.6064 |  | 63.9205 |  | 15.9527 |  | 67.59% |  | – |  | 50.1481
HVAC | kWh/p/mo | ₹/p/mo |  | kWh/p/mo |  | kWh/m²/mo |  | L/p/day |  | L/p/day |  | kWh/p/mo |  | L/p/day |  | /100p/mo |  | % closed |  | ₹/p/mo |  | persons/tech
| +10% ▲ | +5% ▲ |  | +5% ● |  | +10% ▲ |  | -86% ✔ |  | -60% ✔ |  | +35% ✔ |  | -42% ▲ |  | +154% ▲ |  | -32% ▲ |  | – |  | –
DG / Outages | 2025 avg: 98.1 | 2025 avg: 1,286 |  | 2025 avg: 15.46 |  | 2025 avg: 2.52 |  | 2025 avg: 2432.2 |  | 2025 avg: 718.3 |  | 2025 avg: 63.4 |  | 2025 avg: 110.1 |  | 2025 avg: 6.28 |  | 2025 avg: 100.0% |  | 2025 avg: 1,840 |  | 2025 avg: –
Tech Manpower | TIER 5 · OPERATIONAL DETAIL — pyramids (apex = smallest of the top-10) & butterflies (back-to-back comparisons)
Attendance
Building Master
Calc engine
💧 WATER HEATMAP — building meter × month (kL) • darker red = higher use • Δ vs median 2023–25 baseline
| Building |  |  | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | Avg 2026 |  | Baseline |  | Δ |  | Share
| SR-1 |  |  | 264 | 239 | 280 | 201 | 189 | 91 | 224 | 329 |  |  |  |  | 227.125 |  | 388.5 |  | -41.54% |  | 4.953%
| SR-2 |  |  | 267 | 427 | 111 | 100 | 102 | 87 | 125 | 312 |  |  |  |  | 191.375 |  | 199.3333 |  | -3.992% |  | 4.173%
| SR-3 |  |  | 205 | 111 | 8 | 60 | 58 | 60 | 62 | 64 |  |  |  |  | 78.5 |  | 171.3333 |  | -54.18% |  | 1.712%
| SR-4 |  |  | 136 | 136 | 337 | 337 | 233 | 221 | 146 | 194 |  |  |  |  | 217.5 |  | 162.0833 |  | 34.19% |  | 4.743%
| SR-9-10B1A |  |  | 568 | 716 | 835 | 1045 | 781 | 279 | 1320 | 1468 |  |  |  |  | 876.5 |  | 458.75 |  | 91.06% |  | 19.11%
| SR-9-10B1B |  |  | 209 | 73 | 268 | 149 | 167 | 46 | 42 | 45 |  |  |  |  | 124.875 |  | 454.25 |  | -72.51% |  | 2.723%
| SR-11-12CA |  |  | 233 | 285 | 337 | 377 | 358 | 200 | 647 | 710 |  |  |  |  | 393.375 |  | 341.25 |  | 15.27% |  | 8.578%
| SR-11-12CB |  |  | 0 | 101 | 450 | 399 | 205 | 50 | 0 | 0 |  |  |  |  | 150.625 |  | 463.0833 |  | -67.47% |  | 3.285%
| Junior School-1&2 |  |  | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 0.25 |  | 204.3333 |  | -99.88% |  | 0.005452%
| Junior School-3 |  |  | 27 | 22 | 40 | 25 | 28 | 7 | 87 | 120 |  |  |  |  | 44.5 |  | 308.6667 |  | -85.58% |  | 0.9704%
| Senior School-1 |  |  | 101 | 50 | 61 | 90 | 7 | 0 | 78 | 82 |  |  |  |  | 58.625 |  | 367.5 |  | -84.05% |  | 1.278%
| Senior School-2 |  |  | 33 | 41 | 15 | 121 | 272 | 5 | 26 | 45 |  |  |  |  | 69.75 |  | 33.8333 |  | 106.2% |  | 1.521%
| Senior School-3 |  |  | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 |  |  |  |  | 1.625 |  | 98.9167 |  | -98.36% |  | 0.03543%
| Academy Building |  |  | 1 | 25 | 53 | 329 | 224 | 61 | 78 | 38 |  |  |  |  | 101.125 |  | 8.75 |  | 1056% |  | 2.205%
| Commons |  |  | 180 | 186 | 587 | 28 | 73 | 77 | 1089 | 1094 |  |  |  |  | 414.25 |  | 183.25 |  | 126.1% |  | 9.033%
| Swimming Pool |  |  | 526 | 576 | 633 | 661 | 482 | 477 | 1640 | 1559 |  |  |  |  | 819.25 |  | 452.9167 |  | 80.88% |  | 17.86%
| Athletic Centre |  |  | 151 | 121 | 53 | 46 | 106 | 146 | 124 | 54 |  |  |  |  | 100.125 |  | 467.1667 |  | -78.57% |  | 2.183%
| PCM |  |  | 468 | 497 | 520 | 468 | 445 | 589 | 598 | 570 |  |  |  |  | 519.375 |  | 1140.6667 |  | -54.47% |  | 11.33%
| Nursery |  |  | 48 | 33 | 43 | 78 | 204 | 96 | 176 | 209 |  |  |  |  | 110.875 |  | – |  | – |  | 2.418%
| Laundry |  |  | 94 | 98 | 104 | 15 | 87 | 68 | 89 | 135 |  |  |  |  | 86.25 |  | – |  | – |  | 1.881%
⚡ POWER HEATMAP — building meter × month (kWh) • darker red = higher use • Δ vs Avg-2025
| Building |  |  | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | Avg 2026 |  | Avg 2025 |  | Δ |  | Share
| SR1,2,3&4 Emergency |  |  | 480 | 525 | 675 | 653 | 647 | 573 | 631 | 815 |  |  |  |  | 624.875 |  | 537.8333 |  | 16.18% |  | 0.3965%
| SR 9&10A,B 11-12A,B Emergency |  |  | 1154 | 1119 | 1257 | 1253 | 1203 | 1054 | 1234 | 1331 |  |  |  |  | 1200.625 |  | 1150.25 |  | 4.379% |  | 0.7618%
| Laundry |  |  | 2447 | 2920 | 3006 | 3383 | 2839 | 2202 | 2875 | 3382 |  |  |  |  | 2881.75 |  | 2706.5 |  | 6.475% |  | 1.828%
| Substation |  |  | 436 | 602 | 993.3 | 961.7 | 1173 | 1030 | 836 | 933 |  |  |  |  | 870.625 |  | 667.5083 |  | 30.43% |  | 0.5524%
| SR-1 |  |  | 2273 | 3173 | 4616 | 6151 | 5274 | 2391 | 4289 | 4790 |  |  |  |  | 4119.625 |  | 2632 |  | 56.52% |  | 2.614%
| SR-2 |  |  | 2426 | 2719 | 4525 | 6080 | 7229 | 2576 | 3615 | 4692 |  |  |  |  | 4232.75 |  | 3026.4167 |  | 39.86% |  | 2.686%
| SR-3 |  |  | 1858 | 3608 | 3486 | 4748 | 4922 | 2227 | 4090 | 5092 |  |  |  |  | 3753.875 |  | 3216.8333 |  | 16.69% |  | 2.382%
| SR-4 |  |  | 3035 | 5027 | 7021 | 9892 | 10722 | 2915 | 6848 | 6408 |  |  |  |  | 6483.5 |  | 3604.75 |  | 79.86% |  | 4.114%
| SR-9-10A |  |  | 2936 | 4122 | 8610 | 13623 | 4475 | 2951 | 3693 | 3576 |  |  |  |  | 5498.25 |  | 5664.7667 |  | -2.94% |  | 3.488%
| SR-9-10B |  |  | 4053 | 6416 | 9833 | 14587 | 12517 | 1965 | 5778 | 12306 |  |  |  |  | 8431.875 |  | 5468.95 |  | 54.18% |  | 5.35%
| SR-11-12CA |  |  | 3981 | 5304 | 7352 | 9602 | 9997 | 4369 | 4443 | 5498 |  |  |  |  | 6318.25 |  | 4599.4 |  | 37.37% |  | 4.009%
| SR-11-12CB |  |  | 4068 | 7064 | 10129 | 13778 | 14594 | 3887 | 6393 | 8718 |  |  |  |  | 8578.875 |  | 5202.85 |  | 64.89% |  | 5.443%
| Junior School-1,2&3 |  |  | 3679 | 5521 | 10138 | 16196 | 21333 | 4292 | 7078 | 10905 |  |  |  |  | 9892.75 |  | 8438.25 |  | 17.24% |  | 6.277%
| Senior School-1&3 |  |  | 7015 | 5863 | 10663 | 18355 | 19464 | 9012 | 7647 | 8760 |  |  |  |  | 10847.375 |  | 9621.1667 |  | 12.74% |  | 6.882%
| Senior School-2 |  |  | 6053 | 5908 | 8688 | 11663 | 13162 | 7658 | 8075 | 8229 |  |  |  |  | 8679.5 |  | 7514.75 |  | 15.5% |  | 5.507%
| Academy Building |  |  | 14400 | 17500 | 20100 | 21900 | 26200 | 17200 | 18700 | 18300 |  |  |  |  | 19287.5 |  | 18408.3333 |  | 4.776% |  | 12.24%
| Pump House |  |  | 10100 | 9900 | 11000 | 10000 | 9900 | 9800 | 9500 | 11500 |  |  |  |  | 10212.5 |  | 12186.0833 |  | -16.2% |  | 6.48%
| On call |  |  | 837 | 947 | 1077 | 877 | 759.8 | 609 | 909.7 | 10147 |  |  |  |  | 2020.4375 |  | 782.8083 |  | 158.1% |  | 1.282%
| Athletic Centre |  |  | 5755 | 6473 | 8754 | 8861 | 8785 | 7367 | 7545 | 9768 |  |  |  |  | 7913.5 |  | 5689.2583 |  | 39.1% |  | 5.021%
| PCM |  |  | 2527 | 2796 | 3576 | 3870 | 3937 | 3733 | 4140 | 3784 |  |  |  |  | 3545.375 |  | 3302.5833 |  | 7.352% |  | 2.249%
| Irrigation |  |  | 1272 | 1135 | 0 | 1224 | 1365 | 1214 | 1265 | 212 |  |  |  |  | 960.875 |  | 1538.3333 |  | -37.54% |  | 0.6096%
| WTP/STP |  |  | 7000 | 7600 | 7700 | 7800 | 7700 | 3600 | 4300 | 4300 |  |  |  |  | 6250 |  | 7486.5 |  | -16.52% |  | 3.965%
| Commons |  |  | 12770 | 15830 | 19230 | 25480 | 27890 | 19950 | 21650 | 25640 |  |  |  |  | 21055 |  | 25376.8333 |  | -17.03% |  | 13.36%
| Nursary |  |  | 780 | 1440 | 3957 | 8560.3 | 7497.7 | 2035.8 | 2497.9 | 4852 |  |  |  |  | 3952.5875 |  | 2515.2083 |  | 57.15% |  | 2.508%
📋 PER-CAPITA KPI MATRIX — ALL MIS DOMAINS (selected month / YTD average vs Avg-2025 and Avg-2024 baselines)
| Domain |  |  | KPI |  |  |  |  | Unit |  |  |  | Selected |  | Avg 2025 |  | Avg 2024 |  | Δ vs 2025 |  | Status
| Energy |  |  | Grid energy per person |  |  |  |  | kWh/person/month |  |  |  | 108.1108 |  | 98.0646 |  | 136.586 |  | 10.24% |  | ▲ Watch
|  |  |  | Energy bill per person |  |  |  |  | ₹/person/month |  |  |  | 1351.2341 |  | 1286.0409 |  | 1705.8823 |  | 5.069% |  | ▲ Watch
|  |  |  | EPI |  |  |  |  | kWh/m²/month |  |  |  | 2.7802 |  | 2.5218 |  | 3.5124 |  | 10.24% |  | ▲ Watch
|  |  |  | HVAC energy per person |  |  |  |  | kWh/person/month |  |  |  | 16.217 |  | 15.4646 |  | 52.5854 |  | 4.866% |  | ● In line
|  |  |  | Power factor |  |  |  |  | ratio |  |  |  | 0.93619 |  | 0.96442 |  | 0.98417 |  | -2.928% |  | ● In line
|  |  |  | Max-demand utilisation (info) |  |  |  |  | % of sanctioned |  |  |  | 37.23% |  | 40.05% |  | 87.54% |  | -7.051% |  | ✔ Better
| Water |  |  | LPCD |  |  |  |  | L/person/day |  |  |  | 334.1592 |  | 2432.213 |  | 1153.4701 |  | -86.26% |  | ✔ Better
|  |  |  | Borewell draw per person |  |  |  |  | L/person/day |  |  |  | 285.7721 |  | 718.2629 |  | 420.0166 |  | -60.21% |  | ✔ Better
| Treatment & Reuse |  |  | STP recycled per person |  |  |  |  | L/person/day |  |  |  | 63.9205 |  | 110.1111 |  | 87.0237 |  | -41.95% |  | ▲ Watch
|  |  |  | STP share of inlet water |  |  |  |  | % |  |  |  | 18.28% |  | 13.29% |  | 17.16% |  | 37.51% |  | ✔ Better
|  |  |  | WTP treated water per person (info) |  |  |  |  | L/person/day |  |  |  | 261.7335 |  | 260.2699 |  | 297.7419 |  | 0.5623% |  | ● In line
|  |  |  | Drip irrigation per person (info) |  |  |  |  | L/person/day |  |  |  | 59.5845 |  | 146.5409 |  | 97.3534 |  | -59.34% |  | ✔ Better
| Solar & Renewables |  |  | Solar generation per person |  |  |  |  | kWh/person/month |  |  |  | 85.6064 |  | 63.3965 |  | – |  | 35.03% |  | ✔ Better
|  |  |  | Solar offset of grid energy |  |  |  |  | % |  |  |  | 79.18% |  | 64.65% |  | – |  | 22.49% |  | ✔ Better
|  |  |  | Solar savings per person (info) |  |  |  |  | ₹/person/month |  |  |  | 1010.1549 |  | – |  | – |  | – |  | – no data/baseline
| Service Desk |  |  | Complaints per 100 persons |  |  |  |  | per 100 persons/month |  |  |  | 15.9527 |  | 6.2777 |  | 10.6782 |  | 154.1% |  | ▲ Watch
|  |  |  | Closure rate |  |  |  |  | % |  |  |  | 67.59% |  | 100% |  | 98.56% |  | -32.41% |  | ▲ Watch
|  |  |  | Pending complaints per 1,000 persons |  |  |  |  | per 1,000 persons |  |  |  | – |  | 0 |  | 0 |  | – |  | – no data/baseline
|  |  |  | Emergency share of complaints (info) |  |  |  |  | % |  |  |  | 3.241% |  | 2.353% |  | 1.153% |  | 37.73% |  | ▲ Watch
| Manpower & Cost |  |  | Deployment % |  |  |  |  | % |  |  |  | 84.84% |  | 83.11% |  | 86.28% |  | 2.084% |  | ● In line
|  |  |  | Overtime per 100 man-days present |  |  |  |  | hrs/100 man-days |  |  |  | – |  | 22.1827 |  | 34.9762 |  | – |  | – no data/baseline
|  |  |  | Technical manpower cost per person |  |  |  |  | ₹/person/month |  |  |  | – |  | 553.9802 |  | 579.2024 |  | – |  | – no data/baseline
|  |  |  | Tracked OPEX per person |  |  |  |  | ₹/person/month |  |  |  | – |  | 1840.0211 |  | 2285.0847 |  | – |  | – no data/baseline
|  |  |  | Technical manpower budget use (info) |  |  |  |  | % |  |  |  | – |  | 69.48% |  | 76.7% |  | – |  | – no data/baseline
|  |  |  | Persons served per technician (info) |  |  |  |  | persons/technician |  |  |  | 50.1481 |  | – |  | – |  | – |  | – no data/baseline
|  |  |  | DG energy per person (info) |  |  |  |  | kWh/person/month |  |  |  | 0.0081241 |  | 0.36505 |  | 0.73016 |  | -97.77% |  | ✔ Better
Method: per-person = monthly quantity ÷ occupants (LPCD sheet, 1,354); L/person/day uses calendar days. Scores compare the selection with the Avg-2025 row of each source sheet (capped 50–150, direction-aware: lower is better for consumption & cost, higher for PF, STP, solar, closure, deployment). '(info)' KPIs are shown but not scored (no 2025 baseline or known data issue). Tracked OPEX = HT energy bill + technical manpower cost (shown only for months where both are logged).

## Complaints summary
COMPLAINTS SUMMARY · Service Desk Performance 2026 vs 2023–2025
| Month | Number of complains received | Priority |  | Complaints closed | % Emergency | %Non-Critical | Pending | Daily average Nos of Complaints
|  |  | Emergency | Non Critical
| Avg 2023 | 156.75 | 46.5 | 110.25 | 155 | 29.67% | 70.33% | 0 | 5.1272
| Avg 2024 | 144.5833 | 1.6667 | 142.9167 | 142.5 | 1.153% | 98.85% | 0 | 4.664
| Avg 2025 | 85 | 2 | 83 | 85 | 2.353% | 97.65% | 0 | 2.7715
| 2026-01-01 | 144 | 8 | 122 | 139 | 5.556% | 84.72% | 1 | 4.6452
| 2026-02-01 | 122 | 0 | 122 | 119 | 0% | 100% | 3 | 4.3571
2026-03-01
2026-04-01
2026-05-01
| 2026-06-01 | 155 | 5 | 150 | 155 | 3.226% | 96.77% |  | 5.1667
| 2026-07-01 | 168 | 6 | 162 | 127 | 3.571% | 96.43% |  | 5.4194
| 2026-08-01 | 216 | 7 | 156 | 146 | 3.241% | 72.22% |  | 6.9677
2026-09-01
2026-10-01
2026-11-01
2026-12-01
| Avg 2026 | 161 | 5.2 | 142.4 | 137.2 | 3.23% | 88.45% | 2 | 5.3112
| Total 2026 YTD | 805 | 26 | 712 | 686 |  |  | 4
AUDIT SNAPSHOT (live)
[10 empty] | AUDIT SNAPSHOT | Baseline | Current (latest)
[10 empty] | Total Complaints | 111 | 216
[10 empty] | Completed | 111 | 146
[10 empty] | Pending | 0 | 0
Formulas:
Daily average Nos of Complaints = IF([Number of complains received]="","",[Number of complains received]/DAY(EOMONTH([Month],0)))
Note on D8: Audit: Emergency (69) > total received (63). Correct the priority split for Jan-26.

## Building wise water
BUILDING-WISE WATER CONSUMPTION (kL) · 2026 monthly vs 2023–2025 averages
Flow hierarchy: Borewells + STP outlet → WTP / drip irrigation / sports field → building sub-meters downstream of WTP. Blue = monthly meter entry · Baseline = MEDIAN of the 2023–25 monthly averages (robust to the suspect Avg-2025 building values) · tiles follow the month selected on FM_Dashboard (latest logged month when 2026 YTD is selected).
BUILDINGS · AUG 2026 (kL) |  |  | BUILDINGS · 2026 YTD AVG (kL/month) |  |  |  | WTP OUTPUT · AUG 2026 (kL) |  |  |  |  | TOP BUILDING · 2026 YTD AVG |  |  |  |  | METERS REPORTING · SELECTED MONTH |  |  |  | DATA-QUALITY FLAGS OPEN
7028 |  |  | 4585.875 |  |  |  | 10986 |  |  |  |  | SR-9-10B1A |  |  |  |  | 24 |  |  |  | 14
vs baseline +19% |  |  | vs baseline -22% · 8 months logged |  |  |  | building meters cover 64% of WTP output |  |  |  |  | 877 kL/month · 19% of building use |  |  |  |  | latest month logged: Aug-26 |  |  |  | 13 verify Avg-2025 · 1 missing month(s) · 0 other
S No | Location | Group | Avg 2023 | Avg 2024 | Avg 2025 | Baseline (median 23–25) | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | Avg 2026 YTD | Total 2026 YTD | Δ YTD vs Avg 2025 | Δ YTD vs Baseline | Months logged | Data-quality flag
A · BUILDING SUB-METERS (downstream of WTP)
1 | SR-1 | Residence | 145.1667 | 388.5 | 1180.5833 | 388.5 | 264 | 239 | 280 | 201 | 189 | 91 | 224 | 329 |  |  |  |  | 227.125 | 1817 | -80.76% | -41.54% | 8 | VERIFY AVG-2025 (>3× prior yrs)
2 | SR-2 | Residence | 178.5833 | 199.3333 | 1194.8333 | 199.3333 | 267 | 427 | 111 | 100 | 102 | 87 | 125 | 312 |  |  |  |  | 191.375 | 1531 | -83.98% | -3.992% | 8 | VERIFY AVG-2025 (>3× prior yrs)
3 | SR-3 | Residence | 103.0833 | 171.3333 | 1274.9167 | 171.3333 | 205 | 111 | 8 | 60 | 58 | 60 | 62 | 64 |  |  |  |  | 78.5 | 628 | -93.84% | -54.18% | 8 | VERIFY AVG-2025 (>3× prior yrs)
4 | SR-4 | Residence | 105.5 | 162.0833 | 1677.1667 | 162.0833 | 136 | 136 | 337 | 337 | 233 | 221 | 146 | 194 |  |  |  |  | 217.5 | 1740 | -87.03% | 34.19% | 8 | VERIFY AVG-2025 (>3× prior yrs)
5 | SR-9-10B1A | Residence | 455.5 | 458.75 | 2503.1667 | 458.75 | 568 | 716 | 835 | 1045 | 781 | 279 | 1320 | 1468 |  |  |  |  | 876.5 | 7012 | -64.98% | 91.06% | 8 | VERIFY AVG-2025 (>3× prior yrs)
6 | SR-9-10B1B | Residence | 415.4167 | 454.25 | 2943.25 | 454.25 | 209 | 73 | 268 | 149 | 167 | 46 | 42 | 45 |  |  |  |  | 124.875 | 999 | -95.76% | -72.51% | 8 | VERIFY AVG-2025 (>3× prior yrs)
7 | SR-11-12CA | Residence | 341.25 | 328.75 | 2175.4167 | 341.25 | 233 | 285 | 337 | 377 | 358 | 200 | 647 | 710 |  |  |  |  | 393.375 | 3147 | -81.92% | 15.27% | 8 | VERIFY AVG-2025 (>3× prior yrs)
8 | SR-11-12CB | Residence | 388.3333 | 463.0833 | 2811.4167 | 463.0833 | 0 | 101 | 450 | 399 | 205 | 50 | 0 | 0 |  |  |  |  | 150.625 | 1205 | -94.64% | -67.47% | 8 | VERIFY AVG-2025 (>3× prior yrs)
9 | Junior School-1&2 | Academic | 177.75 | 204.3333 | 2368.75 | 204.3333 | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 0.25 | 2 | -99.99% | -99.88% | 8 | VERIFY AVG-2025 (>3× prior yrs)
10 | Junior School-3 | Academic | 265.3333 | 308.6667 | 6906.1667 | 308.6667 | 27 | 22 | 40 | 25 | 28 | 7 | 87 | 120 |  |  |  |  | 44.5 | 356 | -99.36% | -85.58% | 8 | VERIFY AVG-2025 (>3× prior yrs)
11 | Senior School-1 | Academic | 367.5 | 328.4167 | 2929.3333 | 367.5 | 101 | 50 | 61 | 90 | 7 | 0 | 78 | 82 |  |  |  |  | 58.625 | 469 | -98% | -84.05% | 8 | VERIFY AVG-2025 (>3× prior yrs)
12 | Senior School-2 | Academic | 51.7075 | 19.7083 | 33.8333 | 33.8333 | 33 | 41 | 15 | 121 | 272 | 5 | 26 | 45 |  |  |  |  | 69.75 | 558 | 106.2% | 106.2% | 8 | OK
13 | Senior School-3 | Academic | 61.9167 | 98.9167 | 2981.5833 | 98.9167 | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 |  |  |  |  | 1.625 | 13 | -99.95% | -98.36% | 8 | VERIFY AVG-2025 (>3× prior yrs)
14 | Academy Building | Academic | 39 | 8.75 | 0.75 | 8.75 | 1 | 25 | 53 | 329 | 224 | 61 | 78 | 38 |  |  |  |  | 101.125 | 809 | 13383% | 1056% | 8 | OK
15 | Commons | Amenity | 183.25 | 97.4167 | 2679.8333 | 183.25 | 180 | 186 | 587 | 28 | 73 | 77 | 1089 | 1094 |  |  |  |  | 414.25 | 3314 | -84.54% | 126.1% | 8 | VERIFY AVG-2025 (>3× prior yrs)
16 | Swimming Pool | Amenity | 452.9167 | 370 | 650.1667 | 452.9167 | 526 | 576 | 633 | 661 | 482 | 477 | 1640 | 1559 |  |  |  |  | 819.25 | 6554 | 26.01% | 80.88% | 8 | OK
17 | Athletic Centre | Amenity | 652.8333 | 467.1667 | 464.6667 | 467.1667 | 151 | 121 | 53 | 46 | 106 | 146 | 124 | 54 |  |  |  |  | 100.125 | 801 | -78.45% | -78.57% | 8 | OK
18 | PCM | Support | 1081.6667 | 1140.6667 | 1193 | 1140.6667 | 468 | 497 | 520 | 468 | 445 | 589 | 598 | 570 |  |  |  |  | 519.375 | 4155 | -56.46% | -54.47% | 8 | OK
19 | Nursery | Support |  |  |  |  | 48 | 33 | 43 | 78 | 204 | 96 | 176 | 209 |  |  |  |  | 110.875 | 887 |  |  | 8 | OK
20 | Laundry | Support |  |  |  |  | 94 | 98 | 104 | 15 | 87 | 68 | 89 | 135 |  |  |  |  | 86.25 | 690 |  |  | 8 | OK
| Σ BUILDING SUB-METERS |  | 5466.7075 | 5670.125 | 35968.8333 | 5904.5833 | 3511 | 3737 | 4736 | 4529 | 4021 | 2574 | 6551 | 7028 |  |  |  |  | 4585.875 | 36687 | -87.25% | -22.33%
B · PRIMARY USES (fed from borewells + STP outlet)
21 | WTP (treated output) | Primary use | 5010.4167 | 12262.25 | 10719 | 10719 | 8770 | 14597 | 12927 | 12096 | 11615 | 7361 | 8310 | 10986 |  |  |  |  | 10832.75 | 86662 | 1.061% | 1.061% | 8 | OK
22 | Drip irrigation | Primary use | 7038 | 4009.4167 | 6035.1667 | 6035.1667 | 5643 | 6541 | 6091 | 7080 | 7193 | 3865 | 1136 | 2501 |  |  |  |  | 5006.25 | 40050 | -17.05% | -17.05% | 8 | OK
23 | Sports field | Primary use | 3818.8333 | 4664.1667 | 12882.75 | 4664.1667 | 3596 | 0 | 0 | 0 | 0 |  | 0 | [5 empty] | 599.3333 | 3596 | -95.35% | -87.15% | 6 | MISSING MONTH(S)
| Σ PRIMARY USES |  | 15867.25 | 20935.8333 | 29636.9167 | 21418.3333 | 18009 | 21138 | 19018 | 19176 | 18808 | 11226 | 9446 | 13487 |  |  |  |  | 16288.5 | 130308 | -45.04% | -23.95%
C · SOURCES (campus inlet)
24 | Borewells | Source | 11410.1183 | 17298.0333 | 29581.0608 | 17298.0333 | 15002 | 19302.67 | 17647.45 | 18490.49 | 21759.4 | 11528.59 | 15618.59 | 11995 |  |  |  |  | 16418.0238 | 131344.19 | -44.5% | -5.087% | 8 | OK
25 | STP outlet (recycled) | Source | 7230.2692 | 3584 | 4534.8333 | 4534.8333 | 3596 | 5654 | 4885 | 3764 | 1496 | 1929 | 2303 | 2683 |  |  |  |  | 3288.75 | 26310 | -27.48% | -27.48% | 8 | OK
| Σ INLET (borewells + STP outlet) |  | 18640.3875 | 20882.0333 | 34115.8942 | 21832.8667 | 18598 | 24956.67 | 22532.45 | 22254.49 | 23255.4 | 13457.59 | 17921.59 | 14678 |  |  |  |  | 19706.7738 | 157654.19 | -42.24% | -9.738%
D · WATER BALANCE & METER COVERAGE
| Inlet − primary uses (kL) |  | 2773.1375 | -53.8 | 4478.9775 |  | 589 | 3818.67 | 3514.45 | 3078.49 | 4447.4 | 2231.59 | 8475.59 | 1191 |  |  |  |  | 3418.2738 |  |  |  |  | Tank storage change, sprinklers & losses. Negative = more used than metered inlet.
| WTP output − building meters (kL) |  | -456.2908 | 6592.125 | -25249.8333 |  | 5259 | 10860 | 8191 | 7567 | 7594 | 4787 | 1759 | 3958 |  |  |  |  | 6246.875 |  |  |  |  | Un-metered use + softener backwash/regeneration + distribution loss.
| Building sub-meter coverage of WTP |  | 109.1% | 46.24% | 335.6% |  | 40.03% | 25.6% | 36.64% | 37.44% | 34.62% | 34.97% | 78.83% | 63.97% |  |  |  |  | 42.33% |  |  |  |  | Share of WTP output that building meters account for (YTD = months where both exist).
| Meters reporting (of 25) | [5 empty] | 25 | 25 | 25 | 25 | 25 | 24 | 25 | 24 | 0 | 0 | 0 | 0 | [5 empty] | Months with fewer meters are incomplete – totals understate use.
SAME-MONTH YEAR-ON-YEAR · Jan-25 vs Jan-26 (kL)
# | Location | Jan-25 | Jan-26 | Δ kL | Δ % | Note
1 | SR-1 | 192 | 264 | 72 | 37.5%
2 | SR-2 | 133 | 267 | 134 | 100.8%
3 | SR-3 | 202 | 205 | 3 | 1.485%
4 | SR-4 | 84 | 136 | 52 | 61.9%
5 | SR-9-10B1A | 826 | 568 | -258 | -31.23%
6 | SR-9-10B1B | 402 | 209 | -193 | -48.01%
7 | SR-11-12CA | 282 | 233 | -49 | -17.38%
8 | SR-11-12CB | 402 | 0 | -402 | -100%
9 | Junior School-1&2 | 340 | 0 | -340 | -100%
10 | Junior School-3 | 9 | 27 | 18 | 200%
11 | Senior School-1 | 144 | 101 | -43 | -29.86%
12 | Senior School-2 | 21 | 33 | 12 | 57.14%
13 | Senior School-3 | 3 | 0 | -3 | -100%
14 | Academy Building | 318 | 1 | -317 | -99.69%
15 | Commons | 604 | 180 | -424 | -70.2% | Old table had 31 typed; meter table says 180 – verify
16 | Swimming Pool | 345 | 526 | 181 | 52.46%
17 | Athletic Centre | 137 | 151 | 14 | 10.22%
18 | PCM | 578 | 468 | -110 | -19.03%
19 | Nursery |  | 48 |  |  | No Jan-25 history
20 | Laundry |  | 94 |  |  | Meter starts Mar-26
21 | WTP (treated output) | 14183 | 8770 | -5413 | -38.17%
22 | Drip irrigation | 4690 | 5643 | 953 | 20.32%
23 | Sports field | 16890 | 3596 | -13294 | -78.71% | Jan-26 equals STP outlet (3,596) – suspected copy
24 | Borewells | 19290.87 | 15002 | -4288.87 | -22.23%
25 | STP outlet (recycled) | 4704 | 3596 | -1108 | -23.55%
Unlabelled legacy values (were at M63:M67, no location or month) – owner to identify or delete:
| values | 61 | 140 | 122 | 373 | 489
Note on H9: Baseline = MEDIAN(Avg 2023, Avg 2024, Avg 2025). Median is used because many building Avg-2025 values are 5–25× the 2023/2024 figures (flagged amber) and would inflate a mean.
Note on C33: WTP is a primary use of inlet water; building sub-meters sit downstream of it.

## LPCD
LPCD · LITRES PER CAPITA PER DAY
LPCD = monthly litres ÷ occupants ÷ days in month (averages ÷ 365/12). Benchmark 135 LPCD is domestic.
| Month | Water Consumption in Ltrs | No. of occupants | Benchmark | LPCD
| Avg 2023 | 39998605.8333 | 1354 | 135 | 971.2132
| Avg 2024 | 47504705 | 1354 | 135 | 1153.4701
| Avg 2025 | 100168666.6667 | 1354 | 135 | 2432.213
| 2026-01-01 | 40704000 | 1354 | 135 | 969.7432
| 2026-02-01 | 66046000 | 1354 | 135 | 1742.0869
| 2026-03-01 | 19919000 | 1354 | 135 | 474.5557
| 2026-04-01 | 21828000 | 1354 | 135 | 537.3708
| 2026-05-01 | 26607000 | 1354 | 135 | 633.8924
| 2026-06-01 | 12988000 | 1354 | 135 | 319.744
| 2026-07-01 | 9633000 | 1354 | 135 | 229.4992
| 2026-08-01 | 14026000 | 1354 | 135 | 334.1592
| 2026-09-01 |  | 1354 | 135
| 2026-10-01 |  | 1354 | 135
| 2026-11-01 |  | 1354 | 135
| 2026-12-01 |  | 1354 | 135
| Avg 2026 | 26468875 | 1354 | 135 | 655.1314
| Comparison | 2025-07-01 | 2026-02-01
| Water Con in Lt | 82376000 | 66046000
| No of Occupants | 1354 | 1354
| LPCD | 1962.5482 | 1742.0869
| Benchmark (LPCD) | 135 | 135
Formulas:
LPCD = IF(OR([Water Consumption in Ltrs]="",[No. of occupants]=""),"",IFERROR([Water Consumption in Ltrs]/[No. of occupants]/DAY(EOMONTH([Month],0)),""))
Water Consumption in Ltrs = IFERROR(C24/[Water Consumption in Ltrs, row above]/DAY(EOMONTH(C23,0)),"")
No. of occupants = IFERROR(D24/[No. of occupants, row above]/DAY(EOMONTH(D23,0)),"")
Note on C8: Audit: typed value 40,704 kL × 1,000 (was the formula =40704*1000). Link to metered source when available.

## EPI
EPI · ENERGY PERFORMANCE INDEX (kWh / m² / month)
Electricity consumption / Sq.m/month
| Month | Benchmark | kWh/Sq.m/month
| Avg-2024 | 8 | 3.5124
| Avg-2025 | 8 | 2.5218
| 2026-01-01 | 8 | 1.2649
| 2026-02-01 | 8 | 1.8183
| 2026-03-01 | 8 | 2.377
| 2026-04-01 | 8 | 3.7618
| 2026-05-01 | 8 | 4.2191
| 2026-06-01 | 8 | 1.3848
| 2026-07-01 | 8 | 2.3296
| 2026-08-01 | 8 | 2.7802
| 2026-09-01 | 8
| 2026-10-01 | 8
| 2026-11-01 | 8
| 2026-12-01 | 8
| Built-up Area (sq.mtr) |  | 52652.2667
Power consumption / Sq.m/month
| 2025-02-01 | 2026-01-01 | Benchmark
| 2.49 | 1.2649 | 8

## Power data
HT POWER CONSUMPTION & COST
| Month | HT Units in kWh | HT Units in kVAH | PF | Amount | Unit Rate | MD-Recorded | Sanctioned MD
| Avg 2023 |  | 214546.2083 |  | 2534576.875 | 11.8137 | 562 | 1276
| Avg 2024 | 184937.5 | 187911.8333 | 0.98417 | 2309764.6812 | 12.2917 | 1117 | 1276
| Avg 2025 | 132779.5 | 137678 | 0.96442 | 1741299.3826 | 12.6476 | 511.0333 | 1276
| 2026-01-01 | 66600 | 78804 | 0.84513 | 929887.2 | 11.8 | 306 | 1276
| 2026-02-01 | 95736 | 100326 | 0.95425 | 1099602 | 10.9603 | 386 | 1276
| 2026-03-01 | 125154 | 129780 | 0.96436 | 1406695 | 10.8391 | 440 | 1276
| 2026-04-01 | 198066 | 204438 | 0.96883 | 2109953 | 10.3207 | 744 | 1276
| 2026-05-01 | 222144 | 226842 | 0.97929 | 2496490 | 11.0054 | 706 | 1276
| 2026-06-01 | 72912 | 75684 | 0.96337 | 777429 | 10.272 | 321 | 1276
| 2026-07-01 | 122658 | 126318 | 0.97103 | 1501851 | 11.8894 | 451.44 | 1276
| 2026-08-01 | 146382 | 156360 | 0.93619 | 1829571 | 11.701 | 475 | 1276
2026-09-01
2026-10-01
2026-11-01
2026-12-01
| TOTAL 2026 YTD | 1049652 | 1098552 | 0.95549 | 12151478.2 | 11.0614
| Avg 2026 | 131206.5 | 137319 | 0.94781 | 1518934.775 | 11.0614 | 478.68 | 1276
| Avg 2026 ('000) | 131.2065 | 137.319 |  | 1518.9348
| Parameter | 2025-02-01 | 2026-02-01
| KWH | 131316 | 95736
| KVAH | 134268 | 100326
| Amount | 1584362 | 1099602
| Unit Rate | 11.8 | 10.9603
| MD Recorded | 528 | 386
| Sanctiond MD | 1276 | 1276
Note on C5: Audit: original entry 2,219,250 kWh was the 2024 ANNUAL total; converted to monthly average (÷12) to match the other 'Avg' rows.

## Power Building wise
BUILDING-WISE POWER CONSUMPTION (kWh) · 2026
S No | Buildings | Avg 2024 | Avg 2025 | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | Avg 2026 YTD | Building | Feb-25 | Feb-26
1 | SR1,2,3&4 Emergency | 563.8333 | 537.8333 | 480 | 525 | 675 | 653 | 647 | 573 | 631 | 815 |  |  |  |  | 624.875 | SR1,2,3&4 Emgy. | 538 | 525
2 | SR 9&10A,B 11-12A,B Emergency | 2122.5 | 1150.25 | 1154 | 1119 | 1257 | 1253 | 1203 | 1054 | 1234 | 1331 |  |  |  |  | 1200.625 | SR9/10AB,SR11/12A,B Emgy. | 1850 | 1119
3 | Laundry | 2708.75 | 2706.5 | 2447 | 2920 | 3006 | 3383 | 2839 | 2202 | 2875 | 3382 |  |  |  |  | 2881.75 | Laundry | 2964 | 2920
4 | Substation | 212.821 | 667.5083 | 436 | 602 | 993.3 | 961.7 | 1173 | 1030 | 836 | 933 |  |  |  |  | 870.625 | Substation | 667 | 602
5 | SR-1 | 3459.9167 | 2632 | 2273 | 3173 | 4616 | 6151 | 5274 | 2391 | 4289 | 4790 |  |  |  |  | 4119.625 | SR-1 | 3171 | 3173
6 | SR-2 | 4117.75 | 3026.4167 | 2426 | 2719 | 4525 | 6080 | 7229 | 2576 | 3615 | 4692 |  |  |  |  | 4232.75 | SR-2 | 3893 | 2719
7 | SR-3 | 3465.4167 | 3216.8333 | 1858 | 3608 | 3486 | 4748 | 4922 | 2227 | 4090 | 5092 |  |  |  |  | 3753.875 | SR-3 | 4717 | 3608
8 | SR-4 | 4755.3333 | 3604.75 | 3035 | 5027 | 7021 | 9892 | 10722 | 2915 | 6848 | 6408 |  |  |  |  | 6483.5 | SR-4 | 3563 | 5027
9 | SR-9-10A | 8637 | 5664.7667 | 2936 | 4122 | 8610 | 13623 | 4475 | 2951 | 3693 | 3576 |  |  |  |  | 5498.25 | SR-9-10A | 2756.2 | 4122
10 | SR-9-10B | 5749.0833 | 5468.95 | 4053 | 6416 | 9833 | 14587 | 12517 | 1965 | 5778 | 12306 |  |  |  |  | 8431.875 | SR-9-10B | 1991.4 | 6416
11 | SR-11-12CA | 6480.25 | 4599.4 | 3981 | 5304 | 7352 | 9602 | 9997 | 4369 | 4443 | 5498 |  |  |  |  | 6318.25 | SR-11-12CA | 1930.8 | 5304
12 | SR-11-12CB | 6609 | 5202.85 | 4068 | 7064 | 10129 | 13778 | 14594 | 3887 | 6393 | 8718 |  |  |  |  | 8578.875 | SR-11-12CB | 1966.2 | 7064
13 | Junior School-1,2&3 | 7725.9167 | 8438.25 | 3679 | 5521 | 10138 | 16196 | 21333 | 4292 | 7078 | 10905 |  |  |  |  | 9892.75 | Junior School-1,2&3 | 7939 | 5521
14 | Senior School-1&3 | 3561.1667 | 9621.1667 | 7015 | 5863 | 10663 | 18355 | 19464 | 9012 | 7647 | 8760 |  |  |  |  | 10847.375 | Senior School-1&3 | 9997 | 5863
15 | Senior School-2 | 8511.5833 | 7514.75 | 6053 | 5908 | 8688 | 11663 | 13162 | 7658 | 8075 | 8229 |  |  |  |  | 8679.5 | Senior School-2 | 7384 | 5908
16 | Academy Building | 17065.1075 | 18408.3333 | 14400 | 17500 | 20100 | 21900 | 26200 | 17200 | 18700 | 18300 |  |  |  |  | 19287.5 | Academy Building | 14800 | 17500
17 | Pump House | 4781.7492 | 12186.0833 | 10100 | 9900 | 11000 | 10000 | 9900 | 9800 | 9500 | 11500 |  |  |  |  | 10212.5 | Pump House | 14320 | 9900
18 | On call | 630.7117 | 782.8083 | 837 | 947 | 1077 | 877 | 759.8 | 609 | 909.7 | 10147 |  |  |  |  | 2020.4375 | On call | 599.5 | 947
19 | Athletic Centre | 6193.9167 | 5689.2583 | 5755 | 6473 | 8754 | 8861 | 8785 | 7367 | 7545 | 9768 |  |  |  |  | 7913.5 | Athletic Centre | 41 | 6473
20 | PCM | 4665.1667 | 3302.5833 | 2527 | 2796 | 3576 | 3870 | 3937 | 3733 | 4140 | 3784 |  |  |  |  | 3545.375 | PCM | 2544 | 2796
21 | Irrigation | 2003.6667 | 1538.3333 | 1272 | 1135 | 0 | 1224 | 1365 | 1214 | 1265 | 212 |  |  |  |  | 960.875 | Irrigation | 1888 | 1135
22 | Street Lights | 7506.0062 | 5477.425 | 4411.5 | 4728.5 | 5301 | 5490 | 6445 | 5055 | 4811 | 4393 |  |  |  |  | 5079.375 | Street Lights | 5229 | 4728.5
23 | WTP/STP | 12987.2247 | 7486.5 | 7000 | 7600 | 7700 | 7800 | 7700 | 3600 | 4300 | 4300 |  |  |  |  | 6250 | WTP/STP | 10010 | 7600
24 | Commons | 32877.5 | 25376.8333 | 12770 | 15830 | 19230 | 25480 | 27890 | 19950 | 21650 | 25640 |  |  |  |  | 21055 | Commons | 30890 | 15830
25 | Nursary | 303.2475 | 2515.2083 | 780 | 1440 | 3957 | 8560.3 | 7497.7 | 2035.8 | 2497.9 | 4852 |  |  |  |  | 3952.5875 | Nursary | 3364 | 1440
| Total ('000 kWh) | 157.6946 | 146.8156 | 105.7465 | 128.2405 | 171.6873 | 224.988 | 230.0305 | 119.6658 | 142.8436 | 178.331 |  |  |  |  | 162.6916

## Solar Power
SOLAR POWER · GENERATION & EXPORT TO TSSPDCL
SOLAR POWER EXPORTED TO TSSPDCL
Month | KWh | Savings Amount in INR |  | Export tariff (₹/kWh) | 11.8
2026-01-01 | 89214 | 1052725.2
2026-02-01 | 112176 | 1323676.8
2026-03-01 | 144102 | 1700403.6
2026-04-01 | 227564 | 2685255.2
2026-05-01 | 131666 | 1553658.8
2026-06-01 | 128018 | 1510612.4
2026-07-01 | 100380 | 1184484
2026-08-01 | 115911 | 1367749.8
2026-09-01
2026-10-01
2026-11-01
2026-12-01
TOTAL | 1049031 | 12378565.8
Month | 2026-01-01 | 2026-02-01 | 2026-03-01 | 2026-04-01 | 2026-05-01 | 2026-06-01 | 2026-07-01 | 2026-08-01 | 2026-09-01 | 2026-10-01 | 2026-11-01 | 2026-12-01
Plant Name | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh) | Generation (KWh)
AB_BUILDING | 12661 | 21829 | 23491 | 22775 | 24623 | 21433 | 12655 | 19530
ART_AND_MUSIC | 4548 | 4382.9 | 5865 | 5550 | 6223 | 5423 | 4453 | 4783
ATHLETIC_CENTRE | 3745 | 4540.7 | 4727.3 | 4596.4 | 4933.4 | 4353 | 3606 | 3955
COMMONS_BUILDING | 7601 | 17016 | 20874 | 20938 | 22443 | 18821 | 16903 | 17451
FACILITY_BLOCK | 4676 | 4260 | 6824 | 7130 | 7937 | 6907 | 5651 | 6770
Ground_Mount_And_Substation | 42443 | 46210 | 67509 | 52060 | 55073.8 | 50128 | 39351 | 44867
JS_LIBRARY | 6117.6 | 5871 | 4996.4 | 4764.5 | 5081.5 | 4463 | 3711 | 4045
SENIOR_SCHOOL_1 | 3927 | 4386.2 | 4868.7 | 4656.6 | 5111.7 | 3862 | 3737 | 3820
SQUASH_COURT | 3495.1 | 3680 | 4946.3 | 4825.6 | 5312.2 | 4705 | 3820 | 4047
SS_LABORATORY | 6592 | 7325 | 8503 | 8722 | 9067 | 7923 | 6493 | 6643
Total | 95805.7 | 119500.8 | 152604.7 | 136018.1 | 145805.6 | 128018 | 100380 | 115911
Solar Power
Avg 2025 | 2026-01-01 | 2026-02-01 | 2026-03-01 | 2026-04-01 | 2026-05-01 | 2026-06-01 | 2026-07-01 | 2026-08-01 | 2026-09-01 | 2026-10-01 | 2026-11-01 | 2026-12-01
85838.8667 | 95805.7 | 119500.8 | 152604.7 | 136018.1 | 145805.6 | 128018 | 100380 | 115911

## HVAC consumption
HVAC ELECTRICITY CONSUMPTION (kWh)
HVAC BY BUILDING
| Month | JS | SS | SR1 | SR2 | SR3 | SR4 | SR9/10A | SR9/10B | SR11/12CA | SR11/12CB | Nursery | Total (kWh)
| 2024 (Avg) | 12301.067 | 8812.0931 | 2204.9231 | 2221.0385 | 2547.6923 | 3862.6538 | 5883.2538 | 3588.1308 | 4764.0692 | 4377.9846 | 20637.73 | 71200.6362 |  | 2025-02-01 | 2026-02-01
| 2025 (Avg) | 2851.9091 | 2971.5455 | 997.4167 | 1380.1333 | 822.9167 | 777.7667 | 2576.1167 | 2139.2083 | 1793.975 | 1903.7583 | 2724.3333 | 20939.0795 | JS | 942 | 1730
| 2026-01-01 | 550 | 830 | 257 | 358.3 | 87 | 95 | 647 | 376 | 262.5 | 733 | 460 | 4655.8 | SS | 1952 | 2740
| 2026-02-01 | 1730 | 2740 | 694 | 732 | 273 | 478 | 1267 | 1505 | 917 | 1556 | 930 | 12822 | SR1 | 1081 | 694
| 2026-03-01 | 5630 | 7080 | 1918 | 2624 | 1078 | 1879 | 4920 | 5267 | 2639 | 4099 | 1016 | 38150 | SR2 | 1757 | 732
| 2026-04-01 | 9640 | 11590 | 2771 | 4027 | 1640 | 3058 | 7895 | 6713 | 4819 | 6261 | 3960 | 62374 | SR3 | 983 | 273
| 2026-05-01 | 4250 | 2890 | 1351.4 | 4427 | 287 | 1307 | 3153 | 1399 | 1495 | 2327 | 1090 | 23976.4 | SR4 | 582 | 478
| 2026-06-01 | 1280 | 2160 | 1300 | 1552 | 1506 | 1300 | 794 | 243.4 | 735.5 | 1099.5 | 0 | 11970.4 | SR9/10A | 2756 | 1267
| 2026-07-01 | 3850 | 4590 | 1536 | 1701.9 | 1321 | 1090.2 | 3572 | 3524.1 | 1453.3 | 3374.8 | 2820 | 28833.3 | SR9/10B | 1991 | 1505
| 2026-08-01 | 2457 | 4596 | 1137 | 1271 | 485 | 420.28 | 2376 | 2647 | 1331.6 | 2387 | 2850 | 21957.88 | SR11/12CA | 1930 | 917
| 2026-09-01 | [12 empty] | SR11/12CB | 1966 | 1556
| 2026-10-01 | [12 empty] | Nursery | 2450 | 930
2026-11-01
2026-12-01
| Avg 2026 | 3673.375 | 4559.5 | 1370.55 | 2086.65 | 834.625 | 1203.435 | 3078 | 2709.3125 | 1706.6125 | 2729.6625 | 1640.75 | 25592.4725

## Technical manpower cost
Sodexo-Technical- Manpower Services Invoice Amounts | [5 empty] | Sodexo-Commons - Manpower Services Invoice Amounts | [5 empty] | Sodexo-HK- Manpower Services Invoice Amounts
S No | Description | Month | Amount(TINR,000) | Budget |  | S No | Description | Month | Amount | Amount(TINR,000) | Budget | S No | Description | Month | Amount | Amount(TINR,000) | Budget |  |  | Year | Values in TINR
1 | Technical Manpower Services | 2021-11-01 |  | 1505.47 |  | 1 | Commons | 2021-11-01 |  |  | 1505.47 | 1 | House Keeping | 2021-11-01 |  |  | 1505.47 |  |  | Avg.2018
2 | Technical Arc -Flash suit rent & Technical staff PPE Kit | 2021-11-01 |  | 1505.47 |  | 2 | Commons | 2021-11-01 |  |  | 1505.47 | 2 | House Keeping | 2021-11-01 |  |  | 1505.47 |  |  | Avg.2019
2 | Technical Manpower Services | 2021-12-01 |  | 1505.47 |  | 2 | Commons | 2021-12-01 |  |  | 1505.47 | 2 | House Keeping | 2021-12-01 |  |  | 1505.47 |  |  | Avg.2020
3 | Technical Manpower Services | 2022-01-01 |  | 1505.47 |  | 3 | Commons | 2022-01-01 |  |  | 1505.47 | 3 | House Keeping | 2022-01-01 |  |  | 1505.47 |  |  | Avg.2021
4 | Technical Manpower Services | 2022-02-01 |  | 1505.47 |  | 4 | Commons | 2022-02-01 |  |  | 1505.47 | 4 | House Keeping | 2022-02-01 |  |  | 1505.47 |  |  | Avg.2022
5 | Technical Manpower Services | 2022-03-01 |  | 1505.47 |  | 5 | Commons | 2022-03-01 |  |  | 1505.47 | 5 | House Keeping | 2022-03-01 |  |  | 1505.47
6 | Technical Manpower Services | 2022-04-01 |  | 1505.47 |  | 6 | Commons | 2022-04-01 |  |  | 1505.47 | 6 | House Keeping | 2022-04-01 |  |  | 1505.47
7 | Technical Manpower Services | 2022-05-01 |  | 1505.47 |  | 7 | Commons | 2022-05-01 |  |  | 1505.47 | 7 | House Keeping | 2022-05-01 |  |  | 1505.47
8 | Technical Manpower Services | 2022-06-01 |  | 1505.47 |  | 8 | Commons | 2022-06-01 |  |  | 1505.47 | 8 | House Keeping | 2022-06-01 |  |  | 1505.47
9 | Technical Manpower Services | 2022-07-01 |  | 1505.47 |  | 9 | Commons | 2022-07-01 |  |  | 1505.47 | 9 | House Keeping | 2022-07-01 |  |  | 1505.47
10 | Technical Manpower Services | 2022-08-01 | 569.093 | 1505.47 |  | 10 | Commons | 2022-08-01 |  |  | 1505.47 | 10 | House Keeping | 2022-08-01 |  |  | 1505.47
11 | Technical Manpower Services | 2022-09-01 | 551.683 | 1505.47 |  | 11 | Commons | 2022-09-01 |  |  | 1505.47 | 11 | House Keeping | 2022-09-01 |  |  | 1505.47
12 | Technical Manpower Services | 2022-10-01 | 672.941 | 1505.47 | FM included | 12 | Commons | 2022-10-01 |  |  | 1505.47 | 12 | House Keeping | 2022-10-01 |  |  | 1505.47
13 | Technical Manpower Services | 2022-11-01 | 631.901 | 1505.47 | FM yet to join | 13 | Commons | 2022-11-01 |  |  | 1505.47 | 13 | House Keeping | 2022-11-01 |  |  | 1505.47
14 | Technical Manpower Services | 2022-12-01 | 705 | 1505.47 | FM Joined | 14 | Commons | 2022-12-01 |  |  | 1505.47 | 14 | House Keeping | 2022-12-01 |  |  | 1505.47
|  | Average | 626.1236 |  |  |  |  | Average | [5 empty] | Average
TECHNICAL MANPOWER COST · Sodexo & Trident invoices (₹'000)
Sodexo-Technical- Manpower Services Invoice Amounts | [17 empty] | Particular | 2025-02-01 | 2026-02-01
S No | Description | Month | Amount(TINR,000) | Budget (,000) | Budget Utilisation % | [12 empty] | Amount | 797.927 | 747.92
1 | Technical Manpower Services | Avg.23 | 691.52 | 850 | 81.36% | [12 empty] | Budget | 1084.72 | 1079.5317
2 | Technical Manpower Services | Avg.24 | 784.24 | 1022.46 | 76.7%
3 | Technical Manpower Services | Avg.25 | 750.0892 | 1079.5317 | 69.48%
4 | Technical Manpower Services | 2026-01-01 | 728.279 | 1079.5317 | 67.46%
5 | Technical Manpower Services | 2026-02-01 | 747.92 | 1079.5317 | 69.28%
6 | Technical Manpower Services | 2026-03-01
7 | Technical Manpower Services | 2026-04-01
8 | Technical Manpower Services | 2026-05-01
9 | Technical Manpower Services | 2026-06-01
10 | Technical Manpower Services | 2026-07-01
11 | Technical Manpower Services | 2026-08-01
12 | Technical Manpower Services | 2026-09-01
13 | Technical Manpower Services | 2026-10-01
14 | Technical Manpower Services | 2026-11-01
15 | Technical Manpower Services | 2026-12-01
| Technical Manpower Services | Avg-26 | 738.0995 | 1079.5317 | 68.37%
| Total YTD |  | 1476.199 | 2159.0633 | 68.37%
Average
Trident Manpower Services Invoice Amounts
S No | Description | Month | Amount(TINR,000)
1 | Trident Manpower Services | Avg.22 | 691.52
2 | Trident Manpower Services | 2023-01-01 | 251.34
3 | Trident Manpower Services | 2023-02-01 | 255.4
4 | Trident Manpower Services | 2023-03-01 | 237.03
5 | Trident Manpower Services | 2023-04-01
6 | Trident Manpower Services | 2023-05-01
7 | Trident Manpower Services | 2023-06-01
8 | Trident Manpower Services | 2023-07-01
9 | Trident Manpower Services | 2023-08-01
10 | Trident Manpower Services | 2023-09-01
11 | Trident Manpower Services | 2023-10-01 | 574.962
12 | Trident Manpower Services | 2023-11-01
13 | Trident Manpower Services | 2023-12-01
14 | Total |  | 2010.252
|  | Average | 329.683
Note on F6: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F7: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F8: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F9: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F10: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F11: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F12: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F13: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F14: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on F15: Original budget link was lost. Enter verified invoice amount/budget source rather than carrying forward an invalid reference.
Note on E104: Audit: entered as 574,962 (rupees) in a ₹'000 column – converted to 574.962.

## Attendance
TECHNICAL TEAM ATTENDANCE & DEPLOYMENT
| Technical Team Deployment – 2026 | [9 empty] | 2025-01-01 | 2026-02-01
| Month | Total Present | Total Deployed | % Deployment | OT(in Hrs) | OT Value(INR) | Remarks | Headcount | Weekly Offs | % Deployment | 89.66% | 82.02%
| Avg 2023 | 529 | 576 | 91.84% | 120 | 23760.23
| Avg 2024 | 629 | 729 | 86.28% | 220 | 48902 | OT for 15th & 26th Jan
| Avg 2025 | 583.5833 | 702.1667 | 83.11% | 129.4545 | 25749.5455 | OT for 14,26 Jan-25
| 2026-01-01 | 551 | 633 | 87.05% | 120 | 48043 | OT for 27 Feb-25 | 27 | 4
| 2026-02-01 | 529 | 645 | 82.02% | 200 | 48043 | OT For 31 Mar-25 | 27 | 4
| 2026-03-01 | 545 | 653 | 83.46% | 120 |  |  | 27 | 4
| 2026-04-01 | 530 | 676 | 78.4% |  |  | OT For 01,24-May-25 | 26 | 4
| 2026-05-01 | 550 | 655 | 83.97% |  |  | OT 02-Jun-2025 | 26 | 4
| 2026-06-01 | 580 | 663 | 87.48% |  |  |  | 27 | 4
| 2026-07-01 | 595 | 634 | 93.85% |  |  | OT 15 AUG-2025 | 27 | 4
| 2026-08-01 | 543 | 640 | 84.84% |  |  |  | 27 | 4
| 2026-09-01 |  | 702 |  |  |  | OT 02-OCT-2025 | 27 | 4
| 2026-10-01 |  | 702 |  |  |  |  | 26 | 4
2026-11-01
| 2026-12-01 |  | 729 |  |  |  |  | 27 | 4
| Avg 2026 | 552.875 | 666.5455 | 85.13% | 146.6667 | 48043

## DG Units Generated
DG GENERATION & POWER FAILURE MONITORING
| Month | Units Generated |  |  | Diesel Consumed (in ltrs)Avg./ Month | No. of power failures/Month (Avg) | Total Failure Time ( in Hrs)
| Month | 500KVA | 750KVA | Total Units Generated/Month | Diesel Consumed (L) | Power Failures / Month | Failure Time (Hrs)
| Avg 2023 | 469 | 515 | 984 | 322 | 4.1667 | 5.5
| Avg 2024 | 678.818 | 309.818 | 988.636 | 333 | 42 | 37
| Avg 2025 | 352.2727 | 142 | 494.2727 | 178 | 21 | 27.25
| 2026-01-01 | 4325 | 0 | 4325 | 1523 | 10 | 1.0729
| 2026-02-01 | 770 | 0 | 770 | 266 | 7 | 0.22222
| 2026-03-01 | 44 | 0 | 17 | 8735 | 11 | 8.3
| 2026-04-01 | 86 | 45 | 22 | 17490 | 4 | 0.55
| 2026-05-01 | 88 | 0 | 44 | 17820 | 2 | 6.25
| 2026-06-01 | 60 | 0 | 26 | 12010 | 5 | 1.45
| 2026-07-01 | 78 | 0 | 56 | 16390 | 1 | 0.15
| 2026-08-01 | 50 | 100 | 11 | 11435 | 1 | 0.15
2026-09-01
2026-10-01
2026-11-01
2026-12-01
| Avg 2026 | 687.625 | 18.125 | 658.875 | 10708.625 | 5.125 | 2.2681
| TOTAL 2026 YTD | 5501 | 145 | 5271 | 85669 | 41 | 18.1451
|  | 2025-02-01 | 2026-02-01
| 500KVA | 34 | 770
| 750KVA | 0 | 0
| Total units Generated/Month | 34 | 770
| Diesel Consumed (in ltrs)Avg./ Month | 25 | 266

## WQ
PARAMETERS Bore Well | UNITS | DESIRABLE LIMITS | Bore 01 | Bore 02 | Bore 03 | Bore 04 | Bore 05 | Bore 06 | Bore 07 | Bore 08 | Bore 09 | Bore 10
|  |  | 2026-08-01 | 2026-08-01 | 2026-08-01 | 2026-08-01 | 2026-08-01 | 2026-08-01 | 2026-08-01 | 2026-08-01 | 2026-08-01 | 2026-08-01
PHYSICAL
Colour | Hazen | 5 | Colorless | Colorless | Colorless | Colorless | Colorless | Colorless | Colorless | Colorless | Colorless | Colorless
Turbidity | NTU | 1 | 2026-08-01: 912; 2026-08-01: 840
pH |  | 6.5 - 8.5 | 2026-08-01: 360; 2026-08-01: 150
Electrical Conductivity | Us/cm | NS | 2026-08-01: 380; 2026-08-01: 180
CHEMICAL PARAMETERS
HmmTotal Dissolved Solids | mg/l | 500 | 2026-08-01: 86.4; 2026-08-01: 36
Total Hardness as Caco3 | mg/l | 200 | 2026-08-01: 34.6; 2026-08-01: 14.4
Alkalilnity to Phenolphthalein | mg/l | NS | 2026-08-01: 62.3; 2026-08-01: 56.8
Methyl Orange Alkalinity | mg/l | 200 | 2026-08-01: 20.3; 2026-08-01: 19.2
Calcium as Ca, | mg/l | 75 | 2026-08-01: 190; 2026-08-01: 140
Magnesium as Mg | mg/l | 30 | 2026-08-01: 52.7; 2026-08-01: 42.3
Soldium as Na, | mg/l | NS | 2026-08-01: 29.8; 2026-08-01: 26.8
Potassium as K, | mg/l | NS | 2026-08-01: 0.6; 2026-08-01: o.5
Chloride as Cl, | mg/l | 250 | 2026-08-01: 0.07; 2026-08-01: 0.04
Sulphates as S04, | mg/l | 200 | bar: 2026-08-01; 2026-08-01
Nitrates as No3, | mg/l | 45 | 2026-08-01: 2.44; 2026-08-01: 3.11
Fluoride as F | mg/l | 1 | 2026-08-01: 1.38; 2026-08-01: 1.35
Iron | mg/l | 0.3 | 2026-08-01: 0.02; 2026-08-01: 0.02
Silica | mg/l | NS | 2026-08-01: 21.55; 2026-08-01: 18.14
MICROBIOLOGICAL PARAMETERS
Total Bacterial Count | Cfu/ml | NS | 75 x 10 1 | 68 x 10 1 | 81 x 10 1 | 75 x 10 1 | 37 x 10 2 | 47 x 10 1 | 71 x 10 1 | 43 x 10 1 | 55 x 10 1 | 49 x 10 1
Coli form | MPN/100ml | Nil | 3 | 2 | 2 | 2 | 6 | 2 | 2 | Nil | 2 | 2
E coli |  | Absent/100ml | Absent | Absent | 2 | Absent | Absent | Absent | Absent | Absent | Absent | Absent
SWIMMING POOL |  | 2026-01-01 | 2026-02-01 | 2026-03-01 | 2026-04-01 | 2026-05-01 | 2026-06-01 | 2026-07-01 | 2026-08-01 | 2026-09-01 | 2026-10-01 | 2026-11-01
pH | NS | 2026-01-01: 7.76; 2026-03-01: 7.8; 2026-05-01: 7.49; 2026-06-01: 7.78; 2026-07-01: 8.6; 2026-08-01: 8
Total Alkalinity as (Cac03) | mg/l | 2026-01-01: 124.32; 2026-03-01: 247.52; 2026-05-01: 155.4; 2026-06-01: 152.89; 2026-07-01: 276; 2026-08-01: 260
Aluminium as AI | mg/l | 2026-01-01: <0.01; 2026-03-01: < 0.01; 2026-05-01: < 0.01; 2026-06-01: < 0.01; 2026-07-01: < 0.01
Total Residue Chlorine | mg/l | 2026-01-01: 0.3; 2026-03-01: 0.2; 2026-05-01: 0.4; 2026-06-01: 0.5; 2026-07-01: 0.5
Oxygen Observed in 4 hours at 27 C | mg/l | 2026-01-01: 0.8; 2026-03-01: 0.7; 2026-05-01: 0.2; 2026-06-01: 0.5; 2026-07-01: 0.5
Total Dissolved Solids | mg/l | 2026-01-01: 1689; 2026-03-01: 1779; 2026-05-01: 1839; 2026-06-01: 1176; 2026-07-01: 771; 2026-08-01: 980
Chloride as CI | mg/l | 2026-01-01: 919.7; 2026-03-01: 885.45; 2026-05-01: 958.83; 2026-06-01: 543; 2026-07-01: 320; 2026-08-01: 260
Iron as Fe | HAZEN | 2026-01-01: 0.02; 2026-03-01: 0.02; 2026-05-01: 0.02; 2026-06-01: 0.02; 2026-07-01: 0.02; 2026-08-01: 0.06
Heavy metals (as Pb) | NTU | 2026-01-01: <0.001; 2026-03-01: < 0.001; 2026-05-01: < 0.001; 2026-06-01: < 0.001; 2026-07-01: < 0.001
Color Odour Taste | NS | 2026-01-01: Colorless; 2026-03-01: Colorless; 2026-05-01: Colorless; 2026-06-01: Colorless; 2026-07-01: Colorless
Turbidity | NS | 2026-01-01: 1.37; 2026-03-01: 1.41; 2026-05-01: 1.09; 2026-06-01: 1.39; 2026-07-01: 1; 2026-08-01: 0.5
Odour |  | 2026-01-01: Odourless; 2026-03-01: Odourless; 2026-05-01: Odourless; 2026-06-01: Odourless; 2026-07-01: Odourless; 2026-08-01: Odourless
Taste |  | 2026-01-01: Un agreeable; 2026-03-01: Un agreeable; 2026-05-01: Un agreeable; 2026-06-01: Un agreeable; 2026-07-01: Un agreeable; 2026-08-01: Un agreeable
SEWARE WATER - DISCHARGE |  | 2026-03-01: 2024-05-01; 2026-04-01: 2026-02-01; 2026-05-01: 2026-06-01
pH |  | 2026-01-01: 5.5 - 9.0; 2026-03-01: 7.29; 2026-04-01: 7.42; 2026-05-01: 7.5
Electrical conductivity
Total Solids | mg/l | 2026-01-01: 2200
Total dissolved solids (TDS) | mg/l | 2026-01-01: 2100; 2026-03-01: 4071; 2026-04-01: 3079; 2026-05-01: 724
Total suspended solids (TSS) | mg/l | 2026-01-01: 30-100; 2026-03-01: 18; 2026-04-01: 18; 2026-05-01: 20
Chemical Oxygen demand (COD) | mg/l | 2026-01-01: 100-250; 2026-03-01: 110.4; 2026-04-01: 214; 2026-05-01: 50
Biochemical Oxygen demand (BOD) | mg/l | 2026-01-01: 20 -30; 2026-03-01: 19; 2026-04-01: 26; 2026-05-01: 10
Fecal Coliforms | CFU/ml | 2026-01-01: <1000/100
Colour | mg/l | 2026-01-01: colourless
Oil and Grease | mg/l | 2026-01-01: 10-20; 2026-03-01: < 1.00; 2026-04-01: 1044; 2026-05-01: <5
Sulphide content | mg/l | 2026-01-01: 2; 2026-03-01: 786.4; 2026-04-01: 855; 2026-05-01: 42.6
Chromium content | mg/l | 2026-01-01: 2
Chloride content | mg/l | 2026-01-01: 1000; 2026-03-01: 2289.5; 2026-04-01: <1.00; 2026-05-01: 150
Parameters above desirable limit |  | count | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 4 | 0 | 4

## Monthly KPI Report
MONTHLY KPI REPORT · FACILITY MANAGEMENT 2026 (monthly roll-up of all source sheets · 16 KPIs)
Month | Complaints Received | Closure % | Pending Complaints | LPCD | Water Consumption (KL) | Borewell (KL) | HT Units (kWh) | PF | EPI (kWh/m²) | Solar Export (kWh) | Solar Savings (₹) | DG Generation (kWh) | DG Failures | Deployment % | HVAC (kWh) | Tech Manpower (₹000) | Data Completeness % | Data Status
2026-01-01 | 144 | 96.53% | 1 | 969.7432 | 40704 | 15002 | 66600 | 0.84513 | 1.2649 | 89214 | 1052725.2 | 4325 | 10 | 87.05% | 4655.8 | 728.279 | 100% | READY
2026-02-01 | 122 | 97.54% | 3 | 1742.0869 | 66046 | 19302.67 | 95736 | 0.95425 | 1.8183 | 112176 | 1323676.8 | 770 | 7 | 82.02% | 12822 | 747.92 | 100% | READY
2026-03-01 |  |  |  | 474.5557 | 19919 | 17647.45 | 125154 | 0.96436 | 2.377 | 144102 | 1700403.6 | 17 | 11 | 83.46% | 38150 |  | 75% | PARTIAL
2026-04-01 |  |  |  | 537.3708 | 21828 | 18490.49 | 198066 | 0.96883 | 3.7618 | 227564 | 2685255.2 | 22 | 4 | 78.4% | 62374 |  | 75% | PARTIAL
2026-05-01 |  |  |  | 633.8924 | 26607 | 21759.4 | 222144 | 0.97929 | 4.2191 | 131666 | 1553658.8 | 44 | 2 | 83.97% | 23976.4 |  | 75% | PARTIAL
2026-06-01 | 155 | 100% |  | 319.744 | 12988 | 11528.59 | 72912 | 0.96337 | 1.3848 | 128018 | 1510612.4 | 26 | 5 | 87.48% | 11970.4 |  | 87.5% | READY
2026-07-01 | 168 | 75.6% |  | 229.4992 | 9633 | 15618.59 | 122658 | 0.97103 | 2.3296 | 100380 | 1184484 | 56 | 1 | 93.85% | 28833.3 |  | 87.5% | READY
2026-08-01 | 216 | 67.59% |  | 334.1592 | 14026 | 11995 | 146382 | 0.93619 | 2.7802 | 115911 | 1367749.8 | 11 | 1 | 84.84% | 21957.88 |  | 87.5% | READY
2026-09-01 | [16 empty] | 0% | MISSING
2026-10-01 | [16 empty] | 0% | MISSING
2026-11-01 | [16 empty] | 0% | MISSING
2026-12-01 | [16 empty] | 0% | MISSING
Avg 2026 YTD | 161 | 85.22% | 2 | 655.1314 | 26468.875 | 16418.0238 | 131206.5 | 0.95549 | 2.4919 | 131128.875 | 1547320.725 | 658.875 | 5.125 | 85.07% | 25592.4725 | 738.0995 | 85.94%
Total 2026 YTD | 805 |  | 3 |  | 211751 | 131344.19 | 1049652 |  |  | 1049031 | 12378565.8 | 5271 | 41 |  | 204739.78 | 1476.199
SOURCE BENCHMARKS / CONTROL NOTES
KPI | Target / Benchmark | Rule | Source | Control | Monitoring use
LPCD | 135 | ≤ benchmark | LPCD | Lower is better | Monthly water-efficiency KPI
EPI | 8.0 | ≤ benchmark | EPI | Lower is better | Monthly energy-efficiency KPI
Data Completeness | 80% | ≥ threshold | KPI report | Higher is better | Minimum readiness for management review

## Building_Master
BUILDING MASTER — facility map used by FM_Dashboard & PerCapita_Pyramid
Blue cells are inputs. Enter each facility's occupants (beds / regular users) and built-up area to unlock per-building per-capita (LPCD, kWh/person) and per-m² KPIs. Leave blank if unknown — dashboards then show '–'. Residences carry resident students from the 2026-27 roster (192); staff living in the residences are not counted. Where two buildings share one headcount, enter it on the first and name that building under 'Counted with' on the second — the per-person figures are then worked out for the pair.
Facility | Group | Water meter(s) — 'Building wise water' | Power meter — 'Power Building wise' | Occupants (input) | Built-up area m² (input) | Mapping note | Counted with (shared headcount) | Residence block (2026-27 roster)
SR-1 | Residence | SR-1 | SR-1 | 29 |  |  |  | Charminar (with SR-2)
SR-2 | Residence | SR-2 | SR-2 |  |  |  | SR-1 | Charminar (with SR-1)
SR-3 | Residence | SR-3 | SR-3 | 33 |  |  |  | Falaknuma (with SR-4)
SR-4 | Residence | SR-4 | SR-4 |  |  |  | SR-3 | Falaknuma (with SR-3)
SR-9/10 A | Residence | SR-9-10B1A | SR-9-10A | 44 |  | water meter SR-9-10B1A |  | Chowmahalla-2
SR-9/10 B | Residence | SR-9-10B1B | SR-9-10B | 17 |  | water meter SR-9-10B1B |  | Chowmahalla-1
SR-11/12 CA | Residence | SR-11-12CA | SR-11-12CA | 41 |  |  |  | Golconda-2
SR-11/12 CB | Residence | SR-11-12CB | SR-11-12CB | 28 |  |  |  | Golconda-1
Junior School | Academic | Junior School-1&2 + Junior School-3 | Junior School-1,2&3 |  |  | water JS-1&2 + JS-3; power JS-1,2&3
Senior School 1 & 3 | Academic | Senior School-1 + Senior School-3 | Senior School-1&3 |  |  | power meter covers SS-1 & SS-3
Senior School 2 | Academic | Senior School-2 | Senior School-2
Academy Building | Academic | Academy Building | Academy Building
Commons | Amenity | Commons | Commons
Athletic Centre | Amenity | Athletic Centre | Athletic Centre
Swimming Pool | Amenity | Swimming Pool | — (not metered) |  |  | no separate power meter
PCM | Support | PCM | PCM
Nursery | Support | Nursery | Nursary |  |  | power meter 'Nursary'
Laundry | Support | Laundry | Laundry
Campus occupants (LPCD sheet) |  |  |  | 1354
Campus built-up area m² (EPI sheet) |  |  |  |  | 52652.2667
Sum of facility occupants entered |  |  |  | 192
Resident students entered for SR residences (roster total 192) |  |  |  | 192

## MIS_Calc
MIS CALCULATION ENGINE — links every dashboard figure to the source MIS sheets. Do not type here.
|  |  |  | Month list | [83 empty] | Facility list (drop-down source)
FM_Dashboard month | Aug-26 |  |  | 2026 YTD | [83 empty] | All Facilities
FM_Dashboard facility | All Facilities |  |  | Jan-26 | [83 empty] | SR-1
PerCapita_Pyramid month | Aug-26 |  |  | Feb-26 | [83 empty] | SR-2
Latest month with HT power data | Aug-26 |  |  | Mar-26 | [83 empty] | SR-3
Campus built-up area m² | 52652.2667 |  |  | Apr-26 | [83 empty] | SR-4
LPCD benchmark | 135 |  |  | May-26 | [83 empty] | SR-9/10 A
EPI benchmark (kWh/m²/month) | 8 |  |  | Jun-26 | [83 empty] | SR-9/10 B
PF target | 0.95 |  |  | Jul-26 | [83 empty] | SR-11/12 CA
Deployment target | 0.9 |  |  | Aug-26 | [83 empty] | SR-11/12 CB
Closure target | 0.95 |  |  | Sep-26 | [83 empty] | Junior School
Days in FM selection | 31 |  |  | Oct-26 | [83 empty] | Senior School 1 & 3
Days in Pyramid selection | 31 |  |  | Nov-26 | [83 empty] | Senior School 2
Campus occupants | 1354 |  |  | Dec-26 | [83 empty] | Academy Building
Commons
Athletic Centre
A. Monthly fact table (Jan–Dec 2026) + baselines (Avg 2023 / 2024 / 2025) — blank = not yet logged | [87 empty] | Swimming Pool
PCM
Month | Days | Complaints received (count) | Complaints closed (count) | Pending complaints (count) | Emergency complaints (count) | Water consumption (kL) | Occupants (persons) | LPCD (L/person/day) | Borewell draw (kL) | STP outlet (recycled) (kL) | WTP treated output (kL) | Drip irrigation (kL) | HT grid energy (kWh) | HT energy (kVAh) | Power factor (ratio) | HT energy bill (₹) | Energy unit rate (₹/kVAh) | Max demand recorded (kVA) | Sanctioned MD (kVA) | EPI (kWh/m²/month) | Solar generation (kWh) | Solar exported to TSSPDCL (kWh) | Solar savings (₹) | DG units generated (kWh) | Power failures (count) | Power failure time (hrs) | HVAC energy (kWh) | [7 empty] | Technical manpower cost (₹) | Technical manpower budget (₹) | Technical man-days present (man-days) | Technical man-days deployed (man-days) | Deployment % (%) | Overtime (hrs) | Technical headcount (persons) | Data completeness (%) | Grid energy per person (kWh/person/month) | Energy bill per person (₹/person/month) | HVAC energy per person (kWh/person/month) | Max-demand utilisation (% of sanctioned) | Borewell draw per person (L/person/day) | STP recycled per person (L/person/day) | WTP treated water per person (L/person/day) | Drip irrigation per person (L/person/day) | STP share of inlet water (%) | Solar generation per person (kWh/person/month) | Solar offset of grid energy (%) | Solar savings per person (₹/person/month) | Complaints per 100 persons (per 100 persons/month) | Closure rate (%) | Emergency share of complaints (%) | Pending complaints per 1,000 persons (per 1,000 persons) | Technical manpower cost per person (₹/person/month) | Technical manpower budget use (%) | Overtime per 100 man-days present (hrs/100 man-days) | Persons served per technician (persons/technician) | Tracked OPEX: HT energy bill + technical manpower (₹) | Tracked OPEX per person (₹/person/month) | DG energy per person (kWh/person/month) | chart:ht | chart:solar | chart:bore | chart:stp | chart:lpcd | chart:epi | chart:pf | chart:bill | chart:wtp | chart:comp | chart:closed | chart:deploy | chart:pc_kwh | chart:pc_opex | chart:hvac | chart:dg | chart:dgfail | chart:water | LPCD benchmark | EPI benchmark | PF target | Deploy target | Nursery
Jan-26 | 31 | 144 | 139 | 1 | 8 | 40704 | 1354 | 969.7432 | 15002 | 3596 | 8770 | 5643 | 66600 | 78804 | 0.84513 | 929887.2 | 11.8 | 306 | 1276 | 1.2649 | 95805.7 | 89214 | 1052725.2 | 4325 | 10 | 1.0729 | 4655.8 | [7 empty] | 728279 | 1079531.6667 | 551 | 633 | 87.05% | 120 | 27 | 100% | 49.1876 | 686.7705 | 3.4386 | 23.98% | 357.4117 | 85.6721 | 208.9389 | 134.4404 | 19.34% | 70.7575 | 143.9% | 777.4928 | 10.6352 | 96.53% | 5.556% | 0.73855 | 537.8722 | 67.46% | 21.7786 | 50.1481 | 1658166.2 | 1224.6427 | 3.1942 | 66600 | 95805.7 | 15002 | 3596 | 969.7432 | 1.2649 | 0.84513 | 929887.2 | 8770 | 144 | 139 | 87.05% | 49.1876 | 1224.6427 | 4655.8 | 4325 | 10 | 40704 | 135 | 8 | 0.95 | 0.9 | Laundry
Feb-26 | 28 | 122 | 119 | 3 | 0 | 66046 | 1354 | 1742.0869 | 19302.67 | 5654 | 14597 | 6541 | 95736 | 100326 | 0.95425 | 1099602 | 10.9603 | 386 | 1276 | 1.8183 | 119500.8 | 112176 | 1323676.8 | 770 | 7 | 0.22222 | 12822 | [7 empty] | 747920 | 1079531.6667 | 529 | 645 | 82.02% | 200 | 27 | 100% | 70.7061 | 812.1137 | 9.4697 | 30.25% | 509.1441 | 149.1348 | 385.0232 | 172.5311 | 22.66% | 88.2576 | 124.8% | 977.6047 | 9.0103 | 97.54% | 0% | 2.2157 | 552.3781 | 69.28% | 37.8072 | 50.1481 | 1847522 | 1364.4919 | 0.56869 | 95736 | 119500.8 | 19302.67 | 5654 | 1742.0869 | 1.8183 | 0.95425 | 1099602 | 14597 | 122 | 119 | 82.02% | 70.7061 | 1364.4919 | 12822 | 770 | 7 | 66046 | 135 | 8 | 0.95 | 0.9
Mar-26 | 31 |  |  |  |  | 19919 | 1354 | 474.5557 | 17647.45 | 4885 | 12927 | 6091 | 125154 | 129780 | 0.96436 | 1406695 | 10.8391 | 440 | 1276 | 2.377 | 152604.7 | 144102 | 1700403.6 | 17 | 11 | 8.3 | 38150 | [9 empty] | 545 | 653 | 83.46% | 120 | 27 | 75% | 92.4328 | 1038.918 | 28.1758 | 34.48% | 420.4377 | 116.3816 | 307.9764 | 145.1136 | 21.68% | 112.7066 | 121.9% | 1255.8372 | [6 empty] | 22.0183 | 50.1481 |  |  | 0.012555 | 125154 | 152604.7 | 17647.45 | 4885 | 474.5557 | 2.377 | 0.96436 | 1406695 | 12927 | 0 | 0 | 83.46% | 92.4328 | 0 | 38150 | 17 | 11 | 19919 | 135 | 8 | 0.95 | 0.9
Apr-26 | 30 |  |  |  |  | 21828 | 1354 | 537.3708 | 18490.49 | 3764 | 12096 | 7080 | 198066 | 204438 | 0.96883 | 2109953 | 10.3207 | 744 | 1276 | 3.7618 | 136018.1 | 227564 | 2685255.2 | 22 | 4 | 0.55 | 62374 | [9 empty] | 530 | 676 | 78.4% |  | 26 | 75% | 146.2821 | 1558.3109 | 46.0665 | 58.31% | 455.2065 | 92.6637 | 297.7843 | 174.2984 | 16.91% | 100.4565 | 68.67% | 1983.2018 | [7 empty] | 52.0769 |  |  | 0.016248 | 198066 | 136018.1 | 18490.49 | 3764 | 537.3708 | 3.7618 | 0.96883 | 2109953 | 12096 | 0 | 0 | 78.4% | 146.2821 | 0 | 62374 | 22 | 4 | 21828 | 135 | 8 | 0.95 | 0.9
May-26 | 31 |  |  |  |  | 26607 | 1354 | 633.8924 | 21759.4 | 1496 | 11615 | 7193 | 222144 | 226842 | 0.97929 | 2496490 | 11.0054 | 706 | 1276 | 4.2191 | 145805.6 | 131666 | 1553658.8 | 44 | 2 | 6.25 | 23976.4 | [9 empty] | 550 | 655 | 83.97% |  | 26 | 75% | 164.065 | 1843.7888 | 17.7078 | 55.33% | 518.4019 | 35.6411 | 276.7189 | 171.368 | 6.433% | 107.6851 | 65.64% | 1147.4585 | [7 empty] | 52.0769 |  |  | 0.032496 | 222144 | 145805.6 | 21759.4 | 1496 | 633.8924 | 4.2191 | 0.97929 | 2496490 | 11615 | 0 | 0 | 83.97% | 164.065 | 0 | 23976.4 | 44 | 2 | 26607 | 135 | 8 | 0.95 | 0.9
Jun-26 | 30 | 155 | 155 |  | 5 | 12988 | 1354 | 319.744 | 11528.59 | 1929 | 7361 | 3865 | 72912 | 75684 | 0.96337 | 777429 | 10.272 | 321 | 1276 | 1.3848 | 128018 | 128018 | 1510612.4 | 26 | 5 | 1.45 | 11970.4 | [9 empty] | 580 | 663 | 87.48% |  | 27 | 87.5% | 53.8493 | 574.1721 | 8.8408 | 25.16% | 283.8156 | 47.4889 | 181.2161 | 95.1502 | 14.33% | 94.548 | 175.6% | 1115.6665 | 11.4476 | 100% | 3.226% |  |  |  |  | 50.1481 |  |  | 0.019202 | 72912 | 128018 | 11528.59 | 1929 | 319.744 | 1.3848 | 0.96337 | 777429 | 7361 | 155 | 155 | 87.48% | 53.8493 | 0 | 11970.4 | 26 | 5 | 12988 | 135 | 8 | 0.95 | 0.9
Jul-26 | 31 | 168 | 127 |  | 6 | 9633 | 1354 | 229.4992 | 15618.59 | 2303 | 8310 | 1136 | 122658 | 126318 | 0.97103 | 1501851 | 11.8894 | 451.44 | 1276 | 2.3296 | 100380 | 100380 | 1184484 | 56 | 1 | 0.15 | 28833.3 | [9 empty] | 595 | 634 | 93.85% |  | 27 | 87.5% | 90.5894 | 1109.1957 | 21.2949 | 35.38% | 372.1015 | 54.8673 | 197.9797 | 27.0644 | 12.85% | 74.1359 | 81.84% | 874.8035 | 12.4077 | 75.6% | 3.571% |  |  |  |  | 50.1481 |  |  | 0.041359 | 122658 | 100380 | 15618.59 | 2303 | 229.4992 | 2.3296 | 0.97103 | 1501851 | 8310 | 168 | 127 | 93.85% | 90.5894 | 0 | 28833.3 | 56 | 1 | 9633 | 135 | 8 | 0.95 | 0.9
Aug-26 | 31 | 216 | 146 |  | 7 | 14026 | 1354 | 334.1592 | 11995 | 2683 | 10986 | 2501 | 146382 | 156360 | 0.93619 | 1829571 | 11.701 | 475 | 1276 | 2.7802 | 115911 | 115911 | 1367749.8 | 11 | 1 | 0.15 | 21957.88 | [9 empty] | 543 | 640 | 84.84% |  | 27 | 87.5% | 108.1108 | 1351.2341 | 16.217 | 37.23% | 285.7721 | 63.9205 | 261.7335 | 59.5845 | 18.28% | 85.6064 | 79.18% | 1010.1549 | 15.9527 | 67.59% | 3.241% |  |  |  |  | 50.1481 |  |  | 0.0081241 | 146382 | 115911 | 11995 | 2683 | 334.1592 | 2.7802 | 0.93619 | 1829571 | 10986 | 216 | 146 | 84.84% | 108.1108 | 0 | 21957.88 | 11 | 1 | 14026 | 135 | 8 | 0.95 | 0.9
Sep-26 | 30 | [5 empty] | 1354 | [58 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 8 | 0.95 | 0.9
Oct-26 | 31 | [5 empty] | 1354 | [58 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 8 | 0.95 | 0.9
Nov-26 | 30 | [5 empty] | 1354 | [58 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 8 | 0.95 | 0.9
Dec-26 | 31 | [5 empty] | 1354 | [58 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 | 0 | 135 | 8 | 0.95 | 0.9
Avg 2023 | 30.4167 | 156.75 | 155 | 0 | 46.5 | 39998.6058 | 1354 | 971.2132 | 11410.1183 | 7230.2692 | 5010.4167 | 7038 |  | 214546.2083 |  | 2534576.875 | 11.8137 | 562 | 1276 |  |  |  |  | 984 | 4.1667 | 5.5 | [8 empty] | 691520 | 850000 | 529 | 576 | 91.84% | 120 |  |  |  | 1871.9179 |  | 44.04% | 277.0511 | 175.5594 | 121.6588 | 170.8909 | 38.79% |  |  |  | 11.5768 | 98.88% | 29.67% | 0 | 510.7238 | 81.36% | 22.6843 |  | 3226096.875 | 2382.6417 | 0.72674
Avg 2024 | 30.4167 | 144.5833 | 142.5 | 0 | 1.6667 | 47504.705 | 1354 | 1153.4701 | 17298.0333 | 3584 | 12262.25 | 4009.4167 | 184937.5 | 187911.8333 | 0.98417 | 2309764.6812 | 12.2917 | 1117 | 1276 | 3.5124 |  |  |  | 988.636 | 42 | 37 | 71200.6362 | [7 empty] | 784240 | 1022460 | 629 | 729 | 86.28% | 220 |  |  | 136.586 | 1705.8823 | 52.5854 | 87.54% | 420.0166 | 87.0237 | 297.7419 | 97.3534 | 17.16% |  |  |  | 10.6782 | 98.56% | 1.153% | 0 | 579.2024 | 76.7% | 34.9762 |  | 3094004.6812 | 2285.0847 | 0.73016
Avg 2025 | 30.4167 | 85 | 85 | 0 | 2 | 100168.6667 | 1354 | 2432.213 | 29581.0608 | 4534.8333 | 10719 | 6035.1667 | 132779.5 | 137678 | 0.96442 | 1741299.3826 | 12.6476 | 511.0333 | 1276 | 2.5218 | 85838.8667 |  |  | 494.2727 | 21 | 27.25 | 20939.0795 | [7 empty] | 750089.25 | 1079531.6667 | 583.5833 | 702.1667 | 83.11% | 129.4545 |  |  | 98.0646 | 1286.0409 | 15.4646 | 40.05% | 718.2629 | 110.1111 | 260.2699 | 146.5409 | 13.29% | 63.3965 | 64.65% |  | 6.2777 | 100% | 2.353% | 0 | 553.9802 | 69.48% | 22.1827 |  | 2491388.6326 | 1840.0211 | 0.36505
Baseline days = 365/12
B. Selection engine — FM_Dashboard (month in B3) and PerCapita_Pyramid (month in B5)
Key | KPI | Unit | Agg | FM: selected (total/value) | FM: per month | Months logged | Avg 2025 (per month) | Avg 2024 (per month) | FM Δ vs 2025 | PYR: per month | PYR Δ vs 2025 | Avg 2023 (per month)
comp | Complaints received | count | sum | 216 | 216 | 5 | 85 | 144.5833 | 154.1% | 216 | 154.1% | 156.75
closed | Complaints closed | count | sum | 146 | 146 | 5 | 85 | 142.5 | 71.76% | 146 | 71.76% | 155
pend | Pending complaints | count | last |  |  | 2 | 0 | 0 |  |  |  | 0
emerg | Emergency complaints | count | sum | 7 | 7 | 5 | 2 | 1.6667 | 250% | 7 | 250% | 46.5
water | Water consumption | kL | sum | 14026 | 14026 | 8 | 100168.6667 | 47504.705 | -86% | 14026 | -86% | 39998.6058
occ | Occupants | persons | avg | 1354 | 1354 | 12 | 1354 | 1354 | 0% | 1354 | 0% | 1354
lpcd | LPCD | L/person/day | avg | 334.1592 | 334.1592 | 8 | 2432.213 | 1153.4701 | -86.26% | 334.1592 | -86.26% | 971.2132
bore | Borewell draw | kL | sum | 11995 | 11995 | 8 | 29581.0608 | 17298.0333 | -59.45% | 11995 | -59.45% | 11410.1183
stp | STP outlet (recycled) | kL | sum | 2683 | 2683 | 8 | 4534.8333 | 3584 | -40.84% | 2683 | -40.84% | 7230.2692
wtp | WTP treated output | kL | sum | 10986 | 10986 | 8 | 10719 | 12262.25 | 2.491% | 10986 | 2.491% | 5010.4167
drip | Drip irrigation | kL | sum | 2501 | 2501 | 8 | 6035.1667 | 4009.4167 | -58.56% | 2501 | -58.56% | 7038
ht | HT grid energy | kWh | sum | 146382 | 146382 | 8 | 132779.5 | 184937.5 | 10.24% | 146382 | 10.24%
kvah | HT energy (kVAh) | kVAh | sum | 156360 | 156360 | 8 | 137678 | 187911.8333 | 13.57% | 156360 | 13.57% | 214546.2083
pf | Power factor | ratio | ratio | 0.93619 | 0.93619 | 8 | 0.96442 | 0.98417 | -2.928% | 0.93619 | -2.928%
bill | HT energy bill | ₹ | sum | 1829571 | 1829571 | 8 | 1741299.3826 | 2309764.6812 | 5.069% | 1829571 | 5.069% | 2534576.875
rate | Energy unit rate | ₹/kVAh | ratio | 11.701 | 11.701 | 8 | 12.6476 | 12.2917 | -7.484% | 11.701 | -7.484% | 11.8137
md | Max demand recorded | kVA | avg | 475 | 475 | 8 | 511.0333 | 1117 | -7.051% | 475 | -7.051% | 562
smd | Sanctioned MD | kVA | avg | 1276 | 1276 | 8 | 1276 | 1276 | 0% | 1276 | 0% | 1276
epi | EPI | kWh/m²/month | avg | 2.7802 | 2.7802 | 8 | 2.5218 | 3.5124 | 10.24% | 2.7802 | 10.24%
solar | Solar generation | kWh | sum | 115911 | 115911 | 8 | 85838.8667 |  | 35.03% | 115911 | 35.03%
solexp | Solar exported to TSSPDCL | kWh | sum | 115911 | 115911 | 8 |  |  |  | 115911
solsav | Solar savings | ₹ | sum | 1367749.8 | 1367749.8 | 8 |  |  |  | 1367749.8
dg | DG units generated | kWh | sum | 11 | 11 | 8 | 494.2727 | 988.636 | -97.77% | 11 | -97.77% | 984
dgfail | Power failures | count | sum | 1 | 1 | 8 | 21 | 42 | -95.24% | 1 | -95.24% | 4.1667
dghrs | Power failure time | hrs | sum | 0.15 | 0.15 | 8 | 27.25 | 37 | -99.45% | 0.15 | -99.45% | 5.5
hvac | HVAC energy | kWh | sum | 21957.88 | 21957.88 | 8 | 20939.0795 | 71200.6362 | 4.866% | 21957.88 | 4.866%
tech | Technical manpower cost | ₹ | sum |  |  | 2 | 750089.25 | 784240 |  |  |  | 691520
techb | Technical manpower budget | ₹ | sum |  |  | 2 | 1079531.6667 | 1022460 |  |  |  | 850000
present | Technical man-days present | man-days | sum | 543 | 543 | 8 | 583.5833 | 629 | -6.954% | 543 | -6.954% | 529
deployed | Technical man-days deployed | man-days | sum | 640 | 640 | 8 | 702.1667 | 729 | -8.854% | 640 | -8.854% | 576
deploy | Deployment % | % | ratio | 84.84% | 84.84% | 8 | 83.11% | 86.28% | 2.084% | 84.84% | 2.084% | 91.84%
ot | Overtime | hrs | sum |  |  | 3 | 129.4545 | 220 |  |  |  | 120
head | Technical headcount | persons | avg | 27 | 27 | 8 |  |  |  | 27
complete | Data completeness | % | avg | 87.5% | 87.5% | 8 |  |  |  | 87.5%
pc_kwh | Grid energy per person | kWh/person/month | avg | 108.1108 | 108.1108 | 8 | 98.0646 | 136.586 | 10.24% | 108.1108 | 10.24%
pc_bill | Energy bill per person | ₹/person/month | avg | 1351.2341 | 1351.2341 | 8 | 1286.0409 | 1705.8823 | 5.069% | 1351.2341 | 5.069% | 1871.9179
pc_hvac | HVAC energy per person | kWh/person/month | avg | 16.217 | 16.217 | 8 | 15.4646 | 52.5854 | 4.866% | 16.217 | 4.866%
md_util | Max-demand utilisation | % of sanctioned | avg | 37.23% | 37.23% | 8 | 40.05% | 87.54% | -7.051% | 37.23% | -7.051% | 44.04%
pc_bore | Borewell draw per person | L/person/day | avg | 285.7721 | 285.7721 | 8 | 718.2629 | 420.0166 | -60.21% | 285.7721 | -60.21% | 277.0511
pc_stp | STP recycled per person | L/person/day | avg | 63.9205 | 63.9205 | 8 | 110.1111 | 87.0237 | -41.95% | 63.9205 | -41.95% | 175.5594
pc_wtp | WTP treated water per person | L/person/day | avg | 261.7335 | 261.7335 | 8 | 260.2699 | 297.7419 | 0.5623% | 261.7335 | 0.5623% | 121.6588
pc_drip | Drip irrigation per person | L/person/day | avg | 59.5845 | 59.5845 | 8 | 146.5409 | 97.3534 | -59.34% | 59.5845 | -59.34% | 170.8909
stp_share | STP share of inlet water | % | ratio | 18.28% | 18.28% | 8 | 13.29% | 17.16% | 37.51% | 18.28% | 37.51% | 38.79%
pc_solar | Solar generation per person | kWh/person/month | avg | 85.6064 | 85.6064 | 8 | 63.3965 |  | 35.03% | 85.6064 | 35.03%
sol_off | Solar offset of grid energy | % | ratio | 79.18% | 79.18% | 8 | 64.65% |  | 22.49% | 79.18% | 22.49%
pc_solsav | Solar savings per person | ₹/person/month | avg | 1010.1549 | 1010.1549 | 8 |  |  |  | 1010.1549
pc_comp | Complaints per 100 persons | per 100 persons/month | avg | 15.9527 | 15.9527 | 5 | 6.2777 | 10.6782 | 154.1% | 15.9527 | 154.1% | 11.5768
closure | Closure rate | % | ratio | 67.59% | 67.59% | 5 | 100% | 98.56% | -32.41% | 67.59% | -32.41% | 98.88%
emerg_sh | Emergency share of complaints | % | ratio | 3.241% | 3.241% | 5 | 2.353% | 1.153% | 37.73% | 3.241% | 37.73% | 29.67%
pc_pend | Pending complaints per 1,000 persons | per 1,000 persons | last |  |  | 2 | 0 | 0 |  |  |  | 0
pc_tech | Technical manpower cost per person | ₹/person/month | avg |  |  | 2 | 553.9802 | 579.2024 |  |  |  | 510.7238
tech_util | Technical manpower budget use | % | avg |  |  | 2 | 69.48% | 76.7% |  |  |  | 81.36%
ot_pm | Overtime per 100 man-days present | hrs/100 man-days | avg |  |  | 3 | 22.1827 | 34.9762 |  |  |  | 22.6843
pp_tech | Persons served per technician | persons/technician | avg | 50.1481 | 50.1481 | 8 |  |  |  | 50.1481
opex | Tracked OPEX (HT energy bill + technical manpower) | ₹ | sum |  |  | 2 | 2491388.6326 | 3094004.6812 |  |  |  | 3226096.875
pc_opex | Tracked OPEX per person | ₹/person/month | avg |  |  | 2 | 1840.0211 | 2285.0847 |  |  |  | 2382.6417
pc_dg | DG energy per person | kWh/person/month | avg | 0.0081241 | 0.0081241 | 8 | 0.36505 | 0.73016 | -97.77% | 0.0081241 | -97.77% | 0.72674
C1. Water by building meter (kL) — 'Building wise water' rows 11–30
Building | Group | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | Avg 2025 | Baseline (median 23–25) | FM per month | YTD total | Δ vs baseline | Share | PYR per month | Months logged | Avg 2026 YTD
SR-1 | Residence | 264 | 239 | 280 | 201 | 189 | 91 | 224 | 329 |  |  |  |  | 1180.5833 | 388.5 | 329 | 1817 | -15.32% | 4.681% | 329 | 8 | 227.125
SR-2 | Residence | 267 | 427 | 111 | 100 | 102 | 87 | 125 | 312 |  |  |  |  | 1194.8333 | 199.3333 | 312 | 1531 | 56.52% | 4.439% | 312 | 8 | 191.375
SR-3 | Residence | 205 | 111 | 8 | 60 | 58 | 60 | 62 | 64 |  |  |  |  | 1274.9167 | 171.3333 | 64 | 628 | -62.65% | 0.9106% | 64 | 8 | 78.5
SR-4 | Residence | 136 | 136 | 337 | 337 | 233 | 221 | 146 | 194 |  |  |  |  | 1677.1667 | 162.0833 | 194 | 1740 | 19.69% | 2.76% | 194 | 8 | 217.5
SR-9-10B1A | Residence | 568 | 716 | 835 | 1045 | 781 | 279 | 1320 | 1468 |  |  |  |  | 2503.1667 | 458.75 | 1468 | 7012 | 220% | 20.89% | 1468 | 8 | 876.5
SR-9-10B1B | Residence | 209 | 73 | 268 | 149 | 167 | 46 | 42 | 45 |  |  |  |  | 2943.25 | 454.25 | 45 | 999 | -90.09% | 0.6403% | 45 | 8 | 124.875
SR-11-12CA | Residence | 233 | 285 | 337 | 377 | 358 | 200 | 647 | 710 |  |  |  |  | 2175.4167 | 341.25 | 710 | 3147 | 108.1% | 10.1% | 710 | 8 | 393.375
SR-11-12CB | Residence | 0 | 101 | 450 | 399 | 205 | 50 | 0 | 0 |  |  |  |  | 2811.4167 | 463.0833 | 0 | 1205 | -100% | 0% | 0 | 8 | 150.625
Junior School-1&2 | Academic | 0 | 0 | 1 | 0 | 0 | 1 | 0 | 0 |  |  |  |  | 2368.75 | 204.3333 | 0 | 2 | -100% | 0% | 0 | 8 | 0.25
Junior School-3 | Academic | 27 | 22 | 40 | 25 | 28 | 7 | 87 | 120 |  |  |  |  | 6906.1667 | 308.6667 | 120 | 356 | -61.12% | 1.707% | 120 | 8 | 44.5
Senior School-1 | Academic | 101 | 50 | 61 | 90 | 7 | 0 | 78 | 82 |  |  |  |  | 2929.3333 | 367.5 | 82 | 469 | -77.69% | 1.167% | 82 | 8 | 58.625
Senior School-2 | Academic | 33 | 41 | 15 | 121 | 272 | 5 | 26 | 45 |  |  |  |  | 33.8333 | 33.8333 | 45 | 558 | 33% | 0.6403% | 45 | 8 | 69.75
Senior School-3 | Academic | 0 | 0 | 0 | 0 | 0 | 13 | 0 | 0 |  |  |  |  | 2981.5833 | 98.9167 | 0 | 13 | -100% | 0% | 0 | 8 | 1.625
Academy Building | Academic | 1 | 25 | 53 | 329 | 224 | 61 | 78 | 38 |  |  |  |  | 0.75 | 8.75 | 38 | 809 | 334.3% | 0.5407% | 38 | 8 | 101.125
Commons | Amenity | 180 | 186 | 587 | 28 | 73 | 77 | 1089 | 1094 |  |  |  |  | 2679.8333 | 183.25 | 1094 | 3314 | 497% | 15.57% | 1094 | 8 | 414.25
Swimming Pool | Amenity | 526 | 576 | 633 | 661 | 482 | 477 | 1640 | 1559 |  |  |  |  | 650.1667 | 452.9167 | 1559 | 6554 | 244.2% | 22.18% | 1559 | 8 | 819.25
Athletic Centre | Amenity | 151 | 121 | 53 | 46 | 106 | 146 | 124 | 54 |  |  |  |  | 464.6667 | 467.1667 | 54 | 801 | -88.44% | 0.7684% | 54 | 8 | 100.125
PCM | Support | 468 | 497 | 520 | 468 | 445 | 589 | 598 | 570 |  |  |  |  | 1193 | 1140.6667 | 570 | 4155 | -50.03% | 8.11% | 570 | 8 | 519.375
Nursery | Support | 48 | 33 | 43 | 78 | 204 | 96 | 176 | 209 | [6 empty] | 209 | 887 |  | 2.974% | 209 | 8 | 110.875
Laundry | Support | 94 | 98 | 104 | 15 | 87 | 68 | 89 | 135 | [6 empty] | 135 | 690 |  | 1.921% | 135 | 8 | 86.25
C2. Power by building meter (kWh) — 'Power Building wise' rows 3–27, except row 24 (meter retired from the dashboards: row 157 is left blank, its rank key F270 is pinned last)
Building | Avg 2024 | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | Avg 2025 | — | FM per month | YTD total | Δ vs Avg 2025 | Share | PYR per month | Months logged | Avg 2026 YTD
SR1,2,3&4 Emergency | 563.8333 | 480 | 525 | 675 | 653 | 647 | 573 | 631 | 815 |  |  |  |  | 537.8333 |  | 815 | 4999 | 51.53% | 0.4686% | 815 | 8 | 624.875
SR 9&10A,B 11-12A,B Emergency | 2122.5 | 1154 | 1119 | 1257 | 1253 | 1203 | 1054 | 1234 | 1331 |  |  |  |  | 1150.25 |  | 1331 | 9605 | 15.71% | 0.7652% | 1331 | 8 | 1200.625
Laundry | 2708.75 | 2447 | 2920 | 3006 | 3383 | 2839 | 2202 | 2875 | 3382 |  |  |  |  | 2706.5 |  | 3382 | 23054 | 24.96% | 1.944% | 3382 | 8 | 2881.75
Substation | 212.821 | 436 | 602 | 993.3 | 961.7 | 1173 | 1030 | 836 | 933 |  |  |  |  | 667.5083 |  | 933 | 6965 | 39.77% | 0.5364% | 933 | 8 | 870.625
SR-1 | 3459.9167 | 2273 | 3173 | 4616 | 6151 | 5274 | 2391 | 4289 | 4790 |  |  |  |  | 2632 |  | 4790 | 32957 | 81.99% | 2.754% | 4790 | 8 | 4119.625
SR-2 | 4117.75 | 2426 | 2719 | 4525 | 6080 | 7229 | 2576 | 3615 | 4692 |  |  |  |  | 3026.4167 |  | 4692 | 33862 | 55.03% | 2.698% | 4692 | 8 | 4232.75
SR-3 | 3465.4167 | 1858 | 3608 | 3486 | 4748 | 4922 | 2227 | 4090 | 5092 |  |  |  |  | 3216.8333 |  | 5092 | 30031 | 58.29% | 2.927% | 5092 | 8 | 3753.875
SR-4 | 4755.3333 | 3035 | 5027 | 7021 | 9892 | 10722 | 2915 | 6848 | 6408 |  |  |  |  | 3604.75 |  | 6408 | 51868 | 77.77% | 3.684% | 6408 | 8 | 6483.5
SR-9-10A | 8637 | 2936 | 4122 | 8610 | 13623 | 4475 | 2951 | 3693 | 3576 |  |  |  |  | 5664.7667 |  | 3576 | 43986 | -36.87% | 2.056% | 3576 | 8 | 5498.25
SR-9-10B | 5749.0833 | 4053 | 6416 | 9833 | 14587 | 12517 | 1965 | 5778 | 12306 |  |  |  |  | 5468.95 |  | 12306 | 67455 | 125% | 7.075% | 12306 | 8 | 8431.875
SR-11-12CA | 6480.25 | 3981 | 5304 | 7352 | 9602 | 9997 | 4369 | 4443 | 5498 |  |  |  |  | 4599.4 |  | 5498 | 50546 | 19.54% | 3.161% | 5498 | 8 | 6318.25
SR-11-12CB | 6609 | 4068 | 7064 | 10129 | 13778 | 14594 | 3887 | 6393 | 8718 |  |  |  |  | 5202.85 |  | 8718 | 68631 | 67.56% | 5.012% | 8718 | 8 | 8578.875
Junior School-1,2&3 | 7725.9167 | 3679 | 5521 | 10138 | 16196 | 21333 | 4292 | 7078 | 10905 |  |  |  |  | 8438.25 |  | 10905 | 79142 | 29.23% | 6.269% | 10905 | 8 | 9892.75
Senior School-1&3 | 3561.1667 | 7015 | 5863 | 10663 | 18355 | 19464 | 9012 | 7647 | 8760 |  |  |  |  | 9621.1667 |  | 8760 | 86779 | -8.951% | 5.036% | 8760 | 8 | 10847.375
Senior School-2 | 8511.5833 | 6053 | 5908 | 8688 | 11663 | 13162 | 7658 | 8075 | 8229 |  |  |  |  | 7514.75 |  | 8229 | 69436 | 9.505% | 4.731% | 8229 | 8 | 8679.5
Academy Building | 17065.1075 | 14400 | 17500 | 20100 | 21900 | 26200 | 17200 | 18700 | 18300 |  |  |  |  | 18408.3333 |  | 18300 | 154300 | -0.5885% | 10.52% | 18300 | 8 | 19287.5
Pump House | 4781.7492 | 10100 | 9900 | 11000 | 10000 | 9900 | 9800 | 9500 | 11500 |  |  |  |  | 12186.0833 |  | 11500 | 81700 | -5.63% | 6.612% | 11500 | 8 | 10212.5
On call | 630.7117 | 837 | 947 | 1077 | 877 | 759.8 | 609 | 909.7 | 10147 |  |  |  |  | 782.8083 |  | 10147 | 16163.5 | 1196% | 5.834% | 10147 | 8 | 2020.4375
Athletic Centre | 6193.9167 | 5755 | 6473 | 8754 | 8861 | 8785 | 7367 | 7545 | 9768 |  |  |  |  | 5689.2583 |  | 9768 | 63308 | 71.69% | 5.616% | 9768 | 8 | 7913.5
PCM | 4665.1667 | 2527 | 2796 | 3576 | 3870 | 3937 | 3733 | 4140 | 3784 |  |  |  |  | 3302.5833 |  | 3784 | 28363 | 14.58% | 2.175% | 3784 | 8 | 3545.375
Irrigation | 2003.6667 | 1272 | 1135 | 0 | 1224 | 1365 | 1214 | 1265 | 212 |  |  |  |  | 1538.3333 |  | 212 | 7687 | -86.22% | 0.1219% | 212 | 8 | 960.875
WTP/STP | 12987.2247 | 7000 | 7600 | 7700 | 7800 | 7700 | 3600 | 4300 | 4300 |  |  |  |  | 7486.5 |  | 4300 | 50000 | -42.56% | 2.472% | 4300 | 8 | 6250
Commons | 32877.5 | 12770 | 15830 | 19230 | 25480 | 27890 | 19950 | 21650 | 25640 |  |  |  |  | 25376.8333 |  | 25640 | 168440 | 1.037% | 14.74% | 25640 | 8 | 21055
Nursary | 303.2475 | 780 | 1440 | 3957 | 8560.3 | 7497.7 | 2035.8 | 2497.9 | 4852 |  |  |  |  | 2515.2083 |  | 4852 | 31620.7 | 92.91% | 2.789% | 4852 | 8 | 3952.5875
C3. HVAC energy by building (kWh) — 'HVAC consumption'
Building | — | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | Avg 2025 | — | FM per month | YTD total | Δ vs Avg 2025 | Share | PYR per month | Months logged | Avg 2026 YTD
JS |  | 550 | 1730 | 5630 | 9640 | 4250 | 1280 | 3850 | 2457 |  |  |  |  | 2851.9091 |  | 2457 | 29387 | -13.85% | 11.19% | 2457 | 8 | 3673.375
SS |  | 830 | 2740 | 7080 | 11590 | 2890 | 2160 | 4590 | 4596 |  |  |  |  | 2971.5455 |  | 4596 | 36476 | 54.67% | 20.93% | 4596 | 8 | 4559.5
SR1 |  | 257 | 694 | 1918 | 2771 | 1351.4 | 1300 | 1536 | 1137 |  |  |  |  | 997.4167 |  | 1137 | 10964.4 | 13.99% | 5.178% | 1137 | 8 | 1370.55
SR2 |  | 358.3 | 732 | 2624 | 4027 | 4427 | 1552 | 1701.9 | 1271 |  |  |  |  | 1380.1333 |  | 1271 | 16693.2 | -7.907% | 5.788% | 1271 | 8 | 2086.65
SR3 |  | 87 | 273 | 1078 | 1640 | 287 | 1506 | 1321 | 485 |  |  |  |  | 822.9167 |  | 485 | 6677 | -41.06% | 2.209% | 485 | 8 | 834.625
SR4 |  | 95 | 478 | 1879 | 3058 | 1307 | 1300 | 1090.2 | 420.28 |  |  |  |  | 777.7667 |  | 420.28 | 9627.48 | -45.96% | 1.914% | 420.28 | 8 | 1203.435
SR9/10A |  | 647 | 1267 | 4920 | 7895 | 3153 | 794 | 3572 | 2376 |  |  |  |  | 2576.1167 |  | 2376 | 24624 | -7.768% | 10.82% | 2376 | 8 | 3078
SR9/10B |  | 376 | 1505 | 5267 | 6713 | 1399 | 243.4 | 3524.1 | 2647 |  |  |  |  | 2139.2083 |  | 2647 | 21674.5 | 23.74% | 12.05% | 2647 | 8 | 2709.3125
SR11/12CA |  | 262.5 | 917 | 2639 | 4819 | 1495 | 735.5 | 1453.3 | 1331.6 |  |  |  |  | 1793.975 |  | 1331.6 | 13652.9 | -25.77% | 6.064% | 1331.6 | 8 | 1706.6125
SR11/12CB |  | 733 | 1556 | 4099 | 6261 | 2327 | 1099.5 | 3374.8 | 2387 |  |  |  |  | 1903.7583 |  | 2387 | 21837.3 | 25.38% | 10.87% | 2387 | 8 | 2729.6625
Nursery |  | 460 | 930 | 1016 | 3960 | 1090 | 0 | 2820 | 2850 |  |  |  |  | 2724.3333 |  | 2850 | 13126 | 4.613% | 12.98% | 2850 | 8 | 1640.75
C4. Solar generation by plant (kWh) — 'Solar Power' rows 22–31
Plant | — | Jan-26 | Feb-26 | Mar-26 | Apr-26 | May-26 | Jun-26 | Jul-26 | Aug-26 | Sep-26 | Oct-26 | Nov-26 | Dec-26 | — | — | FM per month | YTD total | — | Share | PYR per month | Months logged | Avg 2026 YTD
Ab Building |  | 12661 | 21829 | 23491 | 22775 | 24623 | 21433 | 12655 | 19530 | [6 empty] | 19530 | 158997 |  | 16.85% | 19530 | 8 | 19874.625
Art And Music |  | 4548 | 4382.9 | 5865 | 5550 | 6223 | 5423 | 4453 | 4783 | [6 empty] | 4783 | 41227.9 |  | 4.126% | 4783 | 8 | 5153.4875
Athletic Centre |  | 3745 | 4540.7 | 4727.3 | 4596.4 | 4933.4 | 4353 | 3606 | 3955 | [6 empty] | 3955 | 34456.8 |  | 3.412% | 3955 | 8 | 4307.1
Commons Building |  | 7601 | 17016 | 20874 | 20938 | 22443 | 18821 | 16903 | 17451 | [6 empty] | 17451 | 142047 |  | 15.06% | 17451 | 8 | 17755.875
Facility Block |  | 4676 | 4260 | 6824 | 7130 | 7937 | 6907 | 5651 | 6770 | [6 empty] | 6770 | 50155 |  | 5.841% | 6770 | 8 | 6269.375
Ground Mount And Substation |  | 42443 | 46210 | 67509 | 52060 | 55073.8 | 50128 | 39351 | 44867 | [6 empty] | 44867 | 397641.8 |  | 38.71% | 44867 | 8 | 49705.225
Js Library |  | 6117.6 | 5871 | 4996.4 | 4764.5 | 5081.5 | 4463 | 3711 | 4045 | [6 empty] | 4045 | 39050 |  | 3.49% | 4045 | 8 | 4881.25
Senior School 1 |  | 3927 | 4386.2 | 4868.7 | 4656.6 | 5111.7 | 3862 | 3737 | 3820 | [6 empty] | 3820 | 34369.2 |  | 3.296% | 3820 | 8 | 4296.15
Squash Court |  | 3495.1 | 3680 | 4946.3 | 4825.6 | 5312.2 | 4705 | 3820 | 4047 | [6 empty] | 4047 | 34831.2 |  | 3.491% | 4047 | 8 | 4353.9
Ss Laboratory |  | 6592 | 7325 | 8503 | 8722 | 9067 | 7923 | 6493 | 6643 | [6 empty] | 6643 | 61268 |  | 5.731% | 6643 | 8 | 7658.5
D. Facility view — water & power mapped per facility (Building_Master)
Facility | Group | Water Jan-26 | Water Feb-26 | Water Mar-26 | Water Apr-26 | Water May-26 | Water Jun-26 | Water Jul-26 | Water Aug-26 | Water Sep-26 | Water Oct-26 | Water Nov-26 | Water Dec-26 | Power Jan-26 | Power Feb-26 | Power Mar-26 | Power Apr-26 | Power May-26 | Power Jun-26 | Power Jul-26 | Power Aug-26 | Power Sep-26 | Power Oct-26 | Power Nov-26 | Power Dec-26 | Water FM/month | Water baseline | Water Δ | Power FM/month | Power Avg 2025 | Power Δ | Occupants | Area m² | LPCD | kWh/person/mo | kWh/m²/mo | Water share | Power share | Water PYR/month | Power PYR/month | Water YTD | Power YTD
SR-1 | Residence | 264 | 239 | 280 | 201 | 189 | 91 | 224 | 329 |  |  |  |  | 2273 | 3173 | 4616 | 6151 | 5274 | 2391 | 4289 | 4790 |  |  |  |  | 329 | 388.5 | -15.32% | 4790 | 2632 | 81.99% | 29 |  | 713.0145 | 326.9655 |  | 4.681% | 3.31% | 329 | 4790 | 1817 | 32957
SR-2 | Residence | 267 | 427 | 111 | 100 | 102 | 87 | 125 | 312 |  |  |  |  | 2426 | 2719 | 4525 | 6080 | 7229 | 2576 | 3615 | 4692 |  |  |  |  | 312 | 199.3333 | 56.52% | 4692 | 3026.4167 | 55.03% |  |  | with SR-1 | with SR-1 |  | 4.439% | 3.243% | 312 | 4692 | 1531 | 33862
SR-3 | Residence | 205 | 111 | 8 | 60 | 58 | 60 | 62 | 64 |  |  |  |  | 1858 | 3608 | 3486 | 4748 | 4922 | 2227 | 4090 | 5092 |  |  |  |  | 64 | 171.3333 | -62.65% | 5092 | 3216.8333 | 58.29% | 33 |  | 252.1994 | 348.4848 |  | 0.9106% | 3.519% | 64 | 5092 | 628 | 30031
SR-4 | Residence | 136 | 136 | 337 | 337 | 233 | 221 | 146 | 194 |  |  |  |  | 3035 | 5027 | 7021 | 9892 | 10722 | 2915 | 6848 | 6408 |  |  |  |  | 194 | 162.0833 | 19.69% | 6408 | 3604.75 | 77.77% |  |  | with SR-3 | with SR-3 |  | 2.76% | 4.428% | 194 | 6408 | 1740 | 51868
SR-9/10 A | Residence | 568 | 716 | 835 | 1045 | 781 | 279 | 1320 | 1468 |  |  |  |  | 2936 | 4122 | 8610 | 13623 | 4475 | 2951 | 3693 | 3576 |  |  |  |  | 1468 | 458.75 | 220% | 3576 | 5664.7667 | -36.87% | 44 |  | 1076.2463 | 81.2727 |  | 20.89% | 2.471% | 1468 | 3576 | 7012 | 43986
SR-9/10 B | Residence | 209 | 73 | 268 | 149 | 167 | 46 | 42 | 45 |  |  |  |  | 4053 | 6416 | 9833 | 14587 | 12517 | 1965 | 5778 | 12306 |  |  |  |  | 45 | 454.25 | -90.09% | 12306 | 5468.95 | 125% | 17 |  | 85.389 | 723.8824 |  | 0.6403% | 8.504% | 45 | 12306 | 999 | 67455
SR-11/12 CA | Residence | 233 | 285 | 337 | 377 | 358 | 200 | 647 | 710 |  |  |  |  | 3981 | 5304 | 7352 | 9602 | 9997 | 4369 | 4443 | 5498 |  |  |  |  | 710 | 341.25 | 108.1% | 5498 | 4599.4 | 19.54% | 41 |  | 558.6153 | 134.0976 |  | 10.1% | 3.8% | 710 | 5498 | 3147 | 50546
SR-11/12 CB | Residence | 0 | 101 | 450 | 399 | 205 | 50 | 0 | 0 |  |  |  |  | 4068 | 7064 | 10129 | 13778 | 14594 | 3887 | 6393 | 8718 |  |  |  |  | 0 | 463.0833 | -100% | 8718 | 5202.85 | 67.56% | 28 |  | 0 | 311.3571 |  | 0% | 6.025% | 0 | 8718 | 1205 | 68631
Junior School | Academic | 27 | 22 | 41 | 25 | 28 | 8 | 87 | 120 |  |  |  |  | 3679 | 5521 | 10138 | 16196 | 21333 | 4292 | 7078 | 10905 |  |  |  |  | 120 | 513 | -76.61% | 10905 | 8438.25 | 29.23% | [5 empty] | 1.707% | 7.536% | 120 | 10905 | 358 | 79142
Senior School 1 & 3 | Academic | 101 | 50 | 61 | 90 | 7 | 13 | 78 | 82 |  |  |  |  | 7015 | 5863 | 10663 | 18355 | 19464 | 9012 | 7647 | 8760 |  |  |  |  | 82 | 466.4167 | -82.42% | 8760 | 9621.1667 | -8.951% | [5 empty] | 1.167% | 6.054% | 82 | 8760 | 482 | 86779
Senior School 2 | Academic | 33 | 41 | 15 | 121 | 272 | 5 | 26 | 45 |  |  |  |  | 6053 | 5908 | 8688 | 11663 | 13162 | 7658 | 8075 | 8229 |  |  |  |  | 45 | 33.8333 | 33% | 8229 | 7514.75 | 9.505% | [5 empty] | 0.6403% | 5.687% | 45 | 8229 | 558 | 69436
Academy Building | Academic | 1 | 25 | 53 | 329 | 224 | 61 | 78 | 38 |  |  |  |  | 14400 | 17500 | 20100 | 21900 | 26200 | 17200 | 18700 | 18300 |  |  |  |  | 38 | 8.75 | 334.3% | 18300 | 18408.3333 | -0.5885% | [5 empty] | 0.5407% | 12.65% | 38 | 18300 | 809 | 154300
Commons | Amenity | 180 | 186 | 587 | 28 | 73 | 77 | 1089 | 1094 |  |  |  |  | 12770 | 15830 | 19230 | 25480 | 27890 | 19950 | 21650 | 25640 |  |  |  |  | 1094 | 183.25 | 497% | 25640 | 25376.8333 | 1.037% | [5 empty] | 15.57% | 17.72% | 1094 | 25640 | 3314 | 168440
Athletic Centre | Amenity | 151 | 121 | 53 | 46 | 106 | 146 | 124 | 54 |  |  |  |  | 5755 | 6473 | 8754 | 8861 | 8785 | 7367 | 7545 | 9768 |  |  |  |  | 54 | 467.1667 | -88.44% | 9768 | 5689.2583 | 71.69% | [5 empty] | 0.7684% | 6.751% | 54 | 9768 | 801 | 63308
Swimming Pool | Amenity | 526 | 576 | 633 | 661 | 482 | 477 | 1640 | 1559 | [16 empty] | 1559 | 452.9167 | 244.2% | [8 empty] | 22.18% |  | 1559 |  | 6554
PCM | Support | 468 | 497 | 520 | 468 | 445 | 589 | 598 | 570 |  |  |  |  | 2527 | 2796 | 3576 | 3870 | 3937 | 3733 | 4140 | 3784 |  |  |  |  | 570 | 1140.6667 | -50.03% | 3784 | 3302.5833 | 14.58% | [5 empty] | 8.11% | 2.615% | 570 | 3784 | 4155 | 28363
Nursery | Support | 48 | 33 | 43 | 78 | 204 | 96 | 176 | 209 |  |  |  |  | 780 | 1440 | 3957 | 8560.3 | 7497.7 | 2035.8 | 2497.9 | 4852 |  |  |  |  | 209 |  |  | 4852 | 2515.2083 | 92.91% | [5 empty] | 2.974% | 3.353% | 209 | 4852 | 887 | 31620.7
Laundry | Support | 94 | 98 | 104 | 15 | 87 | 68 | 89 | 135 |  |  |  |  | 2447 | 2920 | 3006 | 3383 | 2839 | 2202 | 2875 | 3382 |  |  |  |  | 135 |  |  | 3382 | 2706.5 | 24.96% | [5 empty] | 1.921% | 2.337% | 135 | 3382 | 690 | 23054
Selected facility drill-down
Month | Water kL | Power kWh | Water (chart) | Power (chart)
Jan-26 | 3511 | 80056 | 3511 | 80056
Feb-26 | 3737 | 101684 | 3737 | 101684
Mar-26 | 4736 | 143684 | 4736 | 143684
Apr-26 | 4529 | 196729.3 | 4529 | 196729.3
May-26 | 4021 | 200837.7 | 4021 | 200837.7
Jun-26 | 2574 | 96730.8 | 2574 | 96730.8
Jul-26 | 6551 | 119356.9 | 6551 | 119356.9
Aug-26 | 7028 | 144700 | 7028 | 144700
Sep-26 |  |  | 0 | 0
Oct-26 |  |  | 0 | 0
Nov-26 |  |  | 0 | 0
Dec-26 |  |  | 0 | 0
Water group | FM per month (kL)
Residence | 3122
Academic | 285
Amenity | 2707
Support | 914
KPI | Avg 2023 | Avg 2024 | Avg 2025 | 2026 YTD
Water | 39.9313 | 47.4247 | 100 | 26.4243
Borewell | 38.5724 | 58.4767 | 100 | 55.5018
HT energy |  | 139.2817 | 100 | 98.8153
HVAC |  | 340.0371 | 100 | 122.2235
WTP treated water | 46.7433 | 114.3973 | 100 | 101.0612
Energy bill | 145.5566 | 132.646 | 100 | 87.23
STP recycled | 159.4385 | 79.0327 | 100 | 72.522
Complaints | 184.4118 | 170.098 | 100 | 189.4118
water helper | Rank | Name | Value |  | power helper | Rank | Name | Value |  | hvac helper | Rank | Name | Value |  | solar helper | Rank | Name | Value
329.0002 | 1 | Swimming Pool | 1559 |  | 815.0002 | 1 | Commons | 25640 |  | 2457.0002 | 1 | SS | 4596 |  | 19530.0002 | 1 | Ground Mount And Substation | 44867
312.0002 | 2 | SR-9-10B1A | 1468 |  | 1331.0003 | 2 | Academy Building | 18300 |  | 4596.0003 | 2 | Nursery | 2850 |  | 4783.0003 | 2 | Ab Building | 19530
64.0003 | 3 | Commons | 1094 |  | 3382.0003 | 3 | SR-9-10B | 12306 |  | 1137.0003 | 3 | SR9/10B | 2647 |  | 3955.0003 | 3 | Commons Building | 17451
194.0003 | 4 | SR-11-12CA | 710 |  | 933.0003 | 4 | Pump House | 11500 |  | 1271.0003 | 4 | JS | 2457 |  | 17451.0003 | 4 | Facility Block | 6770
1468.0003 | 5 | PCM | 570 |  | 4790.0003 | 5 | Junior School-1,2&3 | 10905 |  | 485.0003 | 5 | SR11/12CB | 2387 |  | 6770.0003 | 5 | Ss Laboratory | 6643
45.0003 | 6 | SR-1 | 329 |  | 4692.0003 | 6 | On call | 10147 |  | 420.2803 | 6 | SR9/10A | 2376 |  | 44867.0003 | 6 | Art And Music | 4783
710.0003 | 7 | SR-2 | 312 |  | 5092.0003 | 7 | Athletic Centre | 9768 |  | 2376.0003 | 7 | SR11/12CA | 1331.6 |  | 4045.0003 | 7 | Squash Court | 4047
0.000256 | 8 | Nursery | 209 |  | 6408.0003 | 8 | Senior School-1&3 | 8760 |  | 2647.0003 | 8 | SR2 | 1271 |  | 3820.0003 | 8 | Js Library | 4045
0.000257 | 9 | SR-4 | 194 |  | 3576.0003 | 9 | SR-11-12CB | 8718 |  | 1331.6003 | 9 | SR1 | 1137 |  | 4047.0003 | 9 | Athletic Centre | 3955
120.0003 | 10 | Laundry | 135 |  | 12306.0003 | 10 | Senior School-2 | 8229 |  | 2387.0003 | 10 | SR3 | 485 |  | 6643.0003 | 10 | Senior School 1 | 3820
82.0003 | 11 | Junior School-3 | 120 |  | 5498.0003 | 11 | SR-4 | 6408 |  | 2850.0003 | 11 | SR4 | 420.28
45.0003 | 12 | Senior School-1 | 82 |  | 8718.0003 | 12 | SR-11-12CA | 5498
0.000261 | 13 | SR-3 | 64 |  | 10905.0003 | 13 | SR-3 | 5092
38.0003 | 14 | Athletic Centre | 54 |  | 8760.0003 | 14 | Nursary | 4852
1094.0003 | 15 | Senior School-2 | 45 |  | 8229.0003 | 15 | SR-1 | 4790
1559.0003 | 16 | SR-9-10B1B | 45 |  | 18300.0003 | 16 | SR-2 | 4692
54.0003 | 17 | Academy Building | 38 |  | 11500.0003 | 17 | WTP/STP | 4300
570.0003 | 18 | Senior School-3 | 0 |  | 10147.0003 | 18 | PCM | 3784
209.0003 | 19 | Junior School-1&2 | 0 |  | 9768.0003 | 19 | SR-9-10A | 3576
135.0003 | 20 | SR-11-12CB | 0 |  | 3784.0003 | 20 | Laundry | 3382
[5 empty] | 212.0003 | 21 | SR 9&10A,B 11-12A,B Emergency | 1331
[5 empty] | -0.99973 | 22 | Substation | 933
[5 empty] | 4300.0003 | 23 | SR1,2,3&4 Emergency | 815
[5 empty] | 25640.0003 | 24 | Irrigation | 212
[5 empty] | 4852.0003 | 25 | 0 | 0
E. Per-capita KPI matrix & pyramid scores (PerCapita_Pyramid month; 100 = Avg-2025 baseline)
Key | Category | KPI | Unit | Selected (per month) | Avg 2025 | Avg 2024 | Δ vs 2025 | Direction | Status | Score (0.5–1.5) | Core | Format
pc_kwh | Energy | Grid energy per person | kWh/person/month | 108.1108 | 98.0646 | 136.586 | 10.24% | lower | ▲ Watch | 0.90708 | 1 | 0.0
pc_bill | Energy | Energy bill per person | ₹/person/month | 1351.2341 | 1286.0409 | 1705.8823 | 5.069% | lower | ▲ Watch | 0.95175 | 1 | #,##0
epi | Energy | EPI | kWh/m²/month | 2.7802 | 2.5218 | 3.5124 | 10.24% | lower | ▲ Watch | 0.90708 | 1 | 0.00
pc_hvac | Energy | HVAC energy per person | kWh/person/month | 16.217 | 15.4646 | 52.5854 | 4.866% | lower | ● In line | 0.9536 | 1 | 0.00
pf | Energy | Power factor | ratio | 0.93619 | 0.96442 | 0.98417 | -2.928% | higher | ● In line | 0.97072 | 1 | 0.000
md_util | Energy | Max-demand utilisation | % of sanctioned | 37.23% | 40.05% | 87.54% | -7.051% | lower | ✔ Better | 1.0759 | 0 | 0.0%
lpcd | Water | LPCD | L/person/day | 334.1592 | 2432.213 | 1153.4701 | -86.26% | lower | ✔ Better | 1.5 | 1 | 0.0
pc_bore | Water | Borewell draw per person | L/person/day | 285.7721 | 718.2629 | 420.0166 | -60.21% | lower | ✔ Better | 1.5 | 1 | 0.0
pc_stp | Treatment & Reuse | STP recycled per person | L/person/day | 63.9205 | 110.1111 | 87.0237 | -41.95% | higher | ▲ Watch | 0.58051 | 1 | 0.0
stp_share | Treatment & Reuse | STP share of inlet water | % | 18.28% | 13.29% | 17.16% | 37.51% | higher | ✔ Better | 1.3751 | 1 | 0.0%
pc_wtp | Treatment & Reuse | WTP treated water per person | L/person/day | 261.7335 | 260.2699 | 297.7419 | 0.5623% | lower | ● In line | 0.99441 | 0 | 0.0
pc_drip | Treatment & Reuse | Drip irrigation per person | L/person/day | 59.5845 | 146.5409 | 97.3534 | -59.34% | lower | ✔ Better | 1.5 | 0 | 0.0
pc_solar | Solar & Renewables | Solar generation per person | kWh/person/month | 85.6064 | 63.3965 |  | 35.03% | higher | ✔ Better | 1.3503 | 1 | 0.0
sol_off | Solar & Renewables | Solar offset of grid energy | % | 79.18% | 64.65% |  | 22.49% | higher | ✔ Better | 1.2249 | 1 | 0.0%
pc_solsav | Solar & Renewables | Solar savings per person | ₹/person/month | 1010.1549 |  |  |  | higher | – no data/baseline |  | 0 | #,##0
pc_comp | Service Desk | Complaints per 100 persons | per 100 persons/month | 15.9527 | 6.2777 | 10.6782 | 154.1% | lower | ▲ Watch | 0.5 | 1 | 0.00
closure | Service Desk | Closure rate | % | 67.59% | 100% | 98.56% | -32.41% | higher | ▲ Watch | 0.67593 | 1 | 0.0%
pc_pend | Service Desk | Pending complaints per 1,000 persons | per 1,000 persons |  | 0 | 0 |  | lower | – no data/baseline |  | 1 | 0.00
emerg_sh | Service Desk | Emergency share of complaints | % | 3.241% | 2.353% | 1.153% | 37.73% | lower | ▲ Watch | 0.72605 | 0 | 0.0%
deploy | Manpower & Cost | Deployment % | % | 84.84% | 83.11% | 86.28% | 2.084% | higher | ● In line | 1.0208 | 1 | 0.0%
ot_pm | Manpower & Cost | Overtime per 100 man-days present | hrs/100 man-days |  | 22.1827 | 34.9762 |  | lower | – no data/baseline |  | 1 | 0.0
pc_tech | Manpower & Cost | Technical manpower cost per person | ₹/person/month |  | 553.9802 | 579.2024 |  | lower | – no data/baseline |  | 1 | #,##0
pc_opex | Manpower & Cost | Tracked OPEX per person | ₹/person/month |  | 1840.0211 | 2285.0847 |  | lower | – no data/baseline |  | 1 | #,##0
tech_util | Manpower & Cost | Technical manpower budget use | % |  | 69.48% | 76.7% |  | lower | – no data/baseline |  | 0 | 0.0%
pp_tech | Manpower & Cost | Persons served per technician | persons/technician | 50.1481 |  |  |  | lower | – no data/baseline |  | 0 | 0.0
pc_dg | Manpower & Cost | DG energy per person | kWh/person/month | 0.0081241 | 0.36505 | 0.73016 | -97.77% | lower | ✔ Better | 1.5 | 0 | 0.00
Tier | Name | Score | Status | Headline KPI | Headline value | Core KPIs scored
Tier 3 · Category | Energy | 93.8046 | ▲ Below 2025 | Grid energy per person | 108.1108 | 5
Tier 3 · Category | Water | 150 | ✔ Better than 2025 | LPCD | 334.1592 | 2
Tier 3 · Category | Solar & Renewables | 128.7593 | ✔ Better than 2025 | Solar generation per person | 85.6064 | 2
Tier 3 · Category | Treatment & Reuse | 97.7828 | ● On par with 2025 | STP recycled per person | 63.9205 | 2
Tier 3 · Category | Service Desk | 58.7963 | ▲ Below 2025 | Complaints per 100 persons | 15.9527 | 2
Tier 3 · Category | Manpower & Cost | 102.0839 | ● On par with 2025 | Tracked OPEX per person |  | 1
Tier 2 · Pillar | Utilities | 121.9023 | ✔ Better than 2025
Tier 2 · Pillar | Sustainability | 113.2711 | ✔ Better than 2025
Tier 2 · Pillar | Operations | 80.4401 | ▲ Below 2025
Tier 1 · Apex | Per-Capita Performance Index | 105.2045 | ✔ Better than 2025 | 8 better • 4 in line • 7 watch • 7 no data
F. Pyramid & butterfly chart blocks (PerCapita_Pyramid month)
water helper | k | Name | Value | Spacer | Extra |  | power helper | k | Name | Value | Spacer | Extra
329.0003 | 10 | Laundry | 135 | 712 | 0 |  | 4790.0003 | 10 | SR-11/12 CA | 5498 | 10071 | -4599.4
312.0003 | 9 | SR-4 | 194 | 682.5 | -162.0833 |  | 4692.0003 | 9 | SR-4 | 6408 | 9616 | -3604.75
64.0003 | 8 | Nursery | 209 | 675 | 0 |  | 5092.0003 | 8 | Senior School 2 | 8229 | 8705.5 | -7514.75
194.0003 | 7 | SR-2 | 312 | 623.5 | -199.3333 |  | 6408.0003 | 7 | SR-11/12 CB | 8718 | 8461 | -5202.85
1468.0003 | 6 | SR-1 | 329 | 615 | -388.5 |  | 3576.0003 | 6 | Senior School 1 & 3 | 8760 | 8440 | -9621.1667
45.0003 | 5 | PCM | 570 | 494.5 | -1140.6667 |  | 12306.0003 | 5 | Athletic Centre | 9768 | 7936 | -5689.2583
710.0003 | 4 | SR-11/12 CA | 710 | 424.5 | -341.25 |  | 5498.0003 | 4 | Junior School | 10905 | 7367.5 | -8438.25
0.000333 | 3 | Commons | 1094 | 232.5 | -183.25 |  | 8718.0003 | 3 | SR-9/10 B | 12306 | 6667 | -5468.95
120.0003 | 2 | SR-9/10 A | 1468 | 45.5 | -458.75 |  | 10905.0003 | 2 | Academy Building | 18300 | 3670 | -18408.3333
82.0003 | 1 | Swimming Pool | 1559 | 0 | -452.9167 |  | 8760.0003 | 1 | Commons | 25640 | 0 | -25376.8333
45.0003 | [6 empty] | 8229.0003
38.0003 | [6 empty] | 18300.0003
1094.0003 | [6 empty] | 25640.0003
54.0003 | [6 empty] | 9768.0003
1559.0003 | [6 empty] | 0.00034
570.0003 | [6 empty] | 3784.0003
209.0003 | [6 empty] | 4852.0003
135.0003 | [6 empty] | 3382.0003
solar helper | k | Name | Value | Spacer | Extra |  | hvac helper | k | Name | Value | Spacer | Extra
19530.0004 | 10 | Senior School 1 | 3820 | 20523.5 |  |  | 2457.0004 | 11 | SR4 | 420.28 | 2087.86
4783.0004 | 9 | Athletic Centre | 3955 | 20456 |  |  | 4596.0004 | 10 | SR3 | 485 | 2055.5
3955.0004 | 8 | Js Library | 4045 | 20411 |  |  | 1137.0004 | 9 | SR1 | 1137 | 1729.5
17451.0004 | 7 | Squash Court | 4047 | 20410 |  |  | 1271.0004 | 8 | SR2 | 1271 | 1662.5
6770.0004 | 6 | Art And Music | 4783 | 20042 |  |  | 485.0004 | 7 | SR11/12CA | 1331.6 | 1632.2
44867.0004 | 5 | Ss Laboratory | 6643 | 19112 |  |  | 420.2804 | 6 | SR9/10A | 2376 | 1110
4045.0004 | 4 | Facility Block | 6770 | 19048.5 |  |  | 2376.0004 | 5 | SR11/12CB | 2387 | 1104.5
3820.0004 | 3 | Commons Building | 17451 | 13708 |  |  | 2647.0004 | 4 | JS | 2457 | 1069.5
4047.0004 | 2 | Ab Building | 19530 | 12668.5 |  |  | 1331.6004 | 3 | SR9/10B | 2647 | 974.5
6643.0004 | 1 | Ground Mount And Substation | 44867 | 0 |  |  | 2387.0004 | 2 | Nursery | 2850 | 873
[7 empty] | 2850.0004 | 1 | SS | 4596 | 0
Month | HT grid (left) | Solar (right) | Borewell (left) | STP recycled (right) | Man-days deployed (left) | Man-days present (right)
Jan-26 | -66600 | 95805.7 | -15002 | 3596 | -633 | 551
Feb-26 | -95736 | 119500.8 | -19302.67 | 5654 | -645 | 529
Mar-26 | -125154 | 152604.7 | -17647.45 | 4885 | -653 | 545
Apr-26 | -198066 | 136018.1 | -18490.49 | 3764 | -676 | 530
May-26 | -222144 | 145805.6 | -21759.4 | 1496 | -655 | 550
Jun-26 | -72912 | 128018 | -11528.59 | 1929 | -663 | 580
Jul-26 | -122658 | 100380 | -15618.59 | 2303 | -634 | 595
Aug-26 | -146382 | 115911 | -11995 | 2683 | -640 | 543
Sep-26 | 0 | 0 | 0 | 0 | 0 | 0
Oct-26 | 0 | 0 | 0 | 0 | 0 | 0
Nov-26 | 0 | 0 | 0 | 0 | 0 | 0
Dec-26 | 0 | 0 | 0 | 0 | 0 | 0